## Executive Summary
Executive Summary: Group 04 GEN-2026-PR15 Priority Process Study
Interconnection Customer GEN-2026-PR15 (Group 04) has requested an Interconnection Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR15 generation for total of:
31.36 MW
The minimum cost of interconnecting GEN-2026-PR15 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light Load: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR15 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 07/24/2026
Costs for Wind Requests were allocated using the 29L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4622700% | SPP | Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR15 | 04 SOUTHEAST | 39 | Priority Process | Wind | 31.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.4 | ER | AEP | Clinton Junction-Weatherford Southeast 138kV | None
GEN-2026-PR14 | 04 SOUTHEAST | 38 | Priority Process | Battery/Storage | 43.99 | [9 empty] | ER | OG&E | Sooner - Cleveland 345kV | None
GEN-2026-PR13 | 04 SOUTHEAST | 37 | Priority Process | Wind | 25.96 | [9 empty] | ER | OG&E | Minco 345kV Substation | None
GEN-2026-PR12 | 04 SOUTHEAST | 36 | Priority Process | Wind | 11.96 | [9 empty] | ER | OG&E | NARDINS2 69kV | None
GEN-2026-PR11 | 05 SOUTHWEST | 35 | Priority Process | Wind | 30 | [9 empty] | ER | SPS | Lost Draw 3 115kV substation | None
GEN-2026-PR9 | 05 SOUTHWEST | 34 | Priority Process | Wind | 15.99 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | None
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | [9 empty] | ER | MIDW | South Hays 230kV | None
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345kV Substation | None
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | None
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | None
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | None
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | None
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | None
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR15 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 31.36 | 0 | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 ftlo System Intact | Build new MINCO 9 to MINCO 7 765kV Transformer 1 | 0 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR15 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 31.36 | 0 | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 ftlo System Intact | Build new MINCO 9 to MINCO 7 765kV Transformer 1 | N/A | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR15 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 31.36 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 60.4 | N/A
GEN-2026-PR15 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 31.36 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 60.4 | N/A
GEN-2026-PR15 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 31.36 | 0 | 515425 WWDPST 4 138 514785 WOODWRD4 138 8 ftlo System Intact | Replace the WWDPST 4 to WOODWRD4 138kV Transformer 8 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR15 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 31.36 | 0 | 515425 WWDPST 4 138 514785 WOODWRD4 138 8 ftlo System Intact | Replace the WWDPST 4 to WOODWRD4 138kV Transformer 8 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR15 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 31.36 | 0 | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 ftlo System Intact | Build new MINCO 9 to MINCO 7 765kV Transformer 1 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 60.4
GEN-2026-PR15 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 31.36 | 0 | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 ftlo System Intact | Build new MINCO 9 to MINCO 7 765kV Transformer 1 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 60.4

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR15 PSIS | ERIS | Thermal | 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | 29WP | System Intact | 287 | 287 | 99.78 | 100.15 |  |  |  | Rebuild the WWRDEHV4 to WWDPST 4 138kV Line 1
04ALL | GEN-2026-PR15 PSIS | ERIS | Thermal | 515425 WWDPST 4 138 514785 WOODWRD4 138 8 | 29WP | System Intact | 286 | 286 | 101.6 | 101.97 |  |  |  | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2
04ALL | GEN-2026-PR15 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 121.97 | 122.26 |  |  |  | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
04ALL | GEN-2026-PR15 PSIS | ERIS | Thermal | None | 29L | None | [7 empty] | None
04ALL | GEN-2026-PR15 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR15 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR15 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 26SP | System Intact | 353 | 353 | 102.23 | 102.82 |  |  |  | Build new MINCO 9 to SEMINOLE9 765kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 26SP, 29SP | System Intact | 349 | 395 | 121.15 | 121.73 |  |  |  | Build new MINCO 9 to SEMINOLE9 765kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 29SP | System Intact | 349 | 395 | 119.49 | 120.32 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 2
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 26SP, 29SP | System Intact | 200 | 200 | 114.24 | 114.81 |  |  |  | Build new MINCO 9 to SEMINOLE9 765kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 26SP, 29SP, 29WP | System Intact | 200 | 200 | 150.63 | 151.19 |  |  |  | Build new WWARD9 to VIOLA9 765kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 29SP | System Intact | 200 | 200 | 114.24 | 114.81 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 2
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 29L | System Intact | 200 | 200 | 172.73 | 173.32 |  |  |  | Build new MINCO 9 to MINCO 7 765kV Transformer 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 26SP, 29L, 29SP, 29WP | System Intact | 200 | 200 | 172.73 | 173.32 |  |  |  | Build new BECKHAM7 to CHISHOLM7 345kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 515785 WINDFRM4 138 520999 MOORLND4 138 1 | 29L | System Intact | 268 | 287 | 113.52 | 113.98 |  |  |  | Build new MINCO 9 to MINCO 7 765kV Transformer 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 26SP, 29SP | System Intact | 353 | 353 | 119.8 | 120.37 |  |  |  | Build new MINCO 9 to SEMINOLE9 765kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 29SP | System Intact | 353 | 353 | 118.16 | 118.97 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 2
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP, 29SP | System Intact | 829 | 829 | 111.39 | 111.55 |  |  |  | Build new WWARD9 to VIOLA9 765kV Line 1
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29SP | System Intact | 829 | 829 | 111.39 | 111.55 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 2
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR15 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR15 | GEN-2026-PR15 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | 0 | 0% | 81488001.7662 | 0.0459
GEN-2026-PR15 | GEN-2026-PR15 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WWRDEHV4 to WWDPST 4 138kV Line 1 | Contingent | Rebuild the existing WWRDEHV4 to WWDPST 4 138 kV line 1 (4.4 miles) to a minimum rating of 472 MVA | 0 | 0% | 5280000 | 0.01941
GEN-2026-PR15 | GEN-2026-PR15 PSIS | 04 SOUTHEAST | TBD | ERIS | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2 | Contingent | Add a new phase shifting transformer at Woodward 138 kV with a rating of 421 MVA | 0 | 0% | 4750000 | 0.01941
GEN-2026-PR15 | GEN-2026-PR15 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 0 | 0% | 12238460 | N/A
GEN-2026-PR15 | GEN-2026-PR15 PSIS | 04 SOUTHEAST | TBD | ERIS | Clinton Junction-Weatherford Southeast 138kV Substation GEN-2026-PR15 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR15 (31.36/Wind), into Clinton Junction-Weatherford Southeast 138kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR15 | GEN-2026-PR15 PSIS | 04 SOUTHEAST | TBD | ERIS | Clinton Junction-Weatherford Southeast 138kV Substation GEN-2026-PR15 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR15 (31.36/Wind), into Clinton Junction-Weatherford Southeast 138kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR15 | GEN-2026-PR15 PSIS CF | 04 SOUTHEAST | 504194 | ERIS | Build new MINCO 9 to MINCO 7 765kV Transformer 1 | Contingent | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 1 with a rating of 1650 MVA | 0 | 0% | 61500000 | N/A
GEN-2026-PR15 | GEN-2026-PR15 PSIS CF | 04 SOUTHEAST | 170065/170066 | ERIS | Beckham County - Potter 345 kV Ckt 1 New Line (SPS) | Contingent | Build a 149.6 mile 345 kV Ckt1 new line from Beckham County 345 kV substation to Potter 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 0% | 227051930 | N/A
GEN-2026-PR15 | GEN-2026-PR15 PSIS CF | 04 SOUTHEAST | 504291 | ERIS | Woodward - Viola 765 kV Ckt 1 New Line | Contingent | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 0 | 0% | 883920000 | N/A
GEN-2026-PR15 | GEN-2026-PR15 PSIS CF | 04 SOUTHEAST | 504167 | ERIS | Minco - Seminole 765 kV Ckt 1 New Line | Contingent | Build a 99.8-mile 765 kV Ckt 1 line from Minco to Seminole | 0 | 0% | 580000000 | N/A
Total | [7 empty] | 0 |  | 1856228391.7662

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR15 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | WERE | 36 | 81488001.7662
Contingent | GEN-2026-PR15 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WWRDEHV4 to WWDPST 4 138kV Line 1 | TBD | Rebuild the existing WWRDEHV4 to WWDPST 4 138 kV line 1 (4.4 miles) to a minimum rating of 472 MVA | OKGE | N/A | 5280000
Contingent | GEN-2026-PR15 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2 | TBD | Add a new phase shifting transformer at Woodward 138 kV with a rating of 421 MVA | OKGE | N/A | 4750000
Contingent | GEN-2026-PR15 PSIS CF | Steady State | 04 SOUTHEAST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEP | 4600200% | 12238460
Contingent | GEN-2026-PR15 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Build new MINCO 9 to MINCO 7 765kV Transformer 1 | 504194 | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 1 with a rating of 1650 MVA | OGE | 4821400% | 61500000
Contingent | GEN-2026-PR15 PSIS CF | Steady State | 04 SOUTHEAST | 2024 ITP | ERIS | Beckham County - Potter 345 kV Ckt 1 New Line (SPS) | 170065/170066 | Build a 149.6 mile 345 kV Ckt1 new line from Beckham County 345 kV substation to Potter 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | N/A | 4743400% | 227051930
Contingent | GEN-2026-PR15 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Woodward - Viola 765 kV Ckt 1 New Line | 504291 | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | N/A | 4821400% | 883920000
Contingent | GEN-2026-PR15 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Minco - Seminole 765 kV Ckt 1 New Line | 504167 | Build a 99.8-mile 765 kV Ckt 1 line from Minco to Seminole | N/A | 4821400% | 580000000
Interconnection | GEN-2026-PR15 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR15 PSIS | ERIS | Clinton Junction-Weatherford Southeast 138kV Substation GEN-2026-PR15 Interconnection (TOIF) (AEP) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR15 (31.36/Wind), into Clinton Junction-Weatherford Southeast 138kV Substation | AEP | TBD | TBD
Interconnection | GEN-2026-PR15 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR15 PSIS | ERIS | Clinton Junction-Weatherford Southeast 138kV Substation GEN-2026-PR15 Interconnection (Non-Shared NU) (AEP) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR15 (31.36/Wind), into Clinton Junction-Weatherford Southeast 138kV Substation | AEP | TBD | TBD
1856228391.7662

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504255 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Reactor | Install 150 MVAR reactor at Southwest Shreveport 765 kV substation | 2025 ITP | Yes | N/A | 0.03388 | 4780500% | 15000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504180 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem 765 kV Reactor | Install 150 MVAR reactor at Anthem 765 kV substation | 2025 ITP | Yes | N/A | 0.07512 | 4821400% | 15000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504182 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Reactor | Install 150 MVAR reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | 0.13569 | 4821400% | 15000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504257 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Reactor | Install 150 MVAR reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.09241 | 4780500% | 15000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504245 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | -0.08527 | 4821400% | 13000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504243 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.07775 | 4821400% | 30000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504219 | Line - Crawfish Draw - Phantom 765 kV New Line | Border 345 kV Reactor | Install 100 MVAR reactor at Border 345 kV substation | 2025 ITP | Yes | N/A | 0.03374 | 4780500% | 12000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 500754 | Carpenter 345 kV New Capacitor | Carpenter 345 kV Capacitor | Install 90 MVAR capacitor at Carpenter 345 kV substation | 2025 ITP | Yes | N/A | 0.03344 | 4727000% | 5126042.73
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504221 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 345 kV Reactor | Install 175 MVAR reactor at Crawfish Draw 345 kV substation | 2025 ITP | Yes | N/A | 0.04879 | 4780500% | 16256703.7325
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504302 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Reactor | Install 150 MVAR reactor at Viola 765 kV substation | 2025 ITP | Yes | N/A | 0.07775 | 4821400% | 266653225
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504248 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.6-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | 0.03388 | 4780500% | 1822360000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504162 | Build a 131.3-mile 765 kV Ckt 1 line from Anthem to Seminole Install 765 kV substation at Anthem Install 150 MVAR reactor at Anthem 765 kV substation Install new 345/765 Ckt 1 transformer at Anthem Install new 345/765 Ckt 2 transformer at Anthem Install new 345/765 Ckt 3 transformer at Anthem | Anthem - Seminole 765 kV Ckt 1 New Line | Build a 131.3-mile 765 kV Ckt 1 line from Anthem to Seminole | 2025 ITP | Yes | N/A | 0.07512 | 4821400% | 762120000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504194 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Minco | 2025 ITP | Yes | N/A | 0.03127 | 4821400% | 61500000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504198 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Minco | 2025 ITP | Yes | N/A | 0.03127 | 4821400% | 61500000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504201 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Minco | 2025 ITP | Yes | N/A | 0.03127 | 4821400% | 61500000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504167 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Seminole 765 kV Ckt 1 New Line | Build a 99.8-mile 765 kV Ckt 1 line from Minco to Seminole | 2025 ITP | Yes | N/A | 0.09241 | 4821400% | 580000000
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.07775 | 4821400% | 883920000
GEN-2026-PR15 | 04 SOUTHEAST | ER | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | N/A | 0.18863 | 4600200% | 12238460
GEN-2026-PR15 | 04 SOUTHEAST | ER | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | N/A | 0.03102 | 4586900% | 23239179
GEN-2026-PR15 | 04 SOUTHEAST | ER | 220739 | 122761 | Czech Hall 138 kV Terminal Upgrade | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | N/A | 0.03906 | 4563200% | 223776.17
GEN-2026-PR15 | 04 SOUTHEAST | ER | 220979/220812 | 170065/170066 | Line - Beckham County - Potter -345 kV New Line | Beckham County - Potter 345 kV Ckt 1 New Line (SPS) | Build a 149.6 mile 345 kV Ckt1 new line from Beckham County 345 kV substation to Potter 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | N/A | 0.04132 | 4743400% | 227051930
GEN-2026-PR15 | 04 SOUTHEAST | ER | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | N/A | -0.04679 | 4644600% | 16516041
GEN-2026-PR15 | 04 SOUTHEAST | ER | 210483 | 72018/72019/72020/72021/72023/72024/72027/72031 | Multi - Park Community - Sunshine 138 kV | Revert_Multi - Park Community - Sunshine 138 kV 1-69kV | Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Yes | N/A | 0.04235 | 4629500% | 53471335
GEN-2026-PR15 | 04 SOUTHEAST | ER | TBD | TBD | Rebuild SOUTHRD4 to ROMNOSE4 138kV line 1 | Rebuild SOUTHRD4 to ROMNOSE4 138kV line 1 | Rebuild the SOUTHRD4 to ROMNOSE 138kV line CKT1 (17.28 miles) to a minimum rating of 165 MVA | DISIS-2021-001 | Yes | N/A | -0.04334 | 36 month estimated lead time | 16660667.52

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR15 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00122 | -0.038259 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00361 | -0.11321 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00116 | -0.036378 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00116 | -0.036378 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00023 | -0.0072128 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00549 | 0.17217 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.00283 | 0.088749 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -5e-05 | -0.001568 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -5e-05 | -0.001568 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00051 | 0.015994 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.0005 | 0.01568 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00194 | 0.060838 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00139 | 0.04359 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00044 | -0.013798 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00044 | -0.013798 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00626 | -0.19631 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.00266 | -0.083418 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00011 | 0.0034496 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00011 | 0.0034496 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00017 | 0.0053312 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00023 | 0.0072128 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00018 | 0.0056448 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00019 | 0.0059584 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.0003136 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.0003136 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.0003136 | No
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.0003136 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR15 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR15 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.06416 | 109.9 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR15 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.06531 | 122.26 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR15 PSIS | 04ALL | 1 | 29WP | GEN-2026-PR15 | TO->FROM | 515425 WWDPST 4 138 514785 WOODWRD4 138 8 | 286 | 286 | 0.03324 | 101.97 | System Intact | TDF Impact | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2
Thermal | GEN-2026-PR15 PSIS | 04ALL | 1 | 29WP | GEN-2026-PR15 | TO->FROM | 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | 287 | 287 | 0.03324 | 100.15 | System Intact | TDF Impact | Rebuild the WWRDEHV4 to WWDPST 4 138kV Line 1
Non-Converged | GEN-2026-PR15 PSIS | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR15 PSIS | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR15 PSIS | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR15 PSIS | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR15 PSIS | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08729 | 121.73 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08729 | 120.37 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03887 | 107.56 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03345 | 103.53 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.08808 | 102.82 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08835 | 120.32 | System Intact | TDF Impact | Beckham County - Potter 345 kV Ckt 1 New Line (SPS)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08835 | 118.97 | System Intact | TDF Impact | Beckham County - Potter 345 kV Ckt 1 New Line (SPS)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03678 | 114.81 | System Intact | TDF Impact | Beckham County - Potter 345 kV Ckt 1 New Line (SPS)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03274 | 111.55 | System Intact | TDF Impact | Beckham County - Potter 345 kV Ckt 1 New Line (SPS)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29WP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03309 | 151.19 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03439 | 173.32 | System Intact | TDF Impact | Build new MINCO 9 to MINCO 7 765kV Transformer 1
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR15 | TO->FROM | 515785 WINDFRM4 138 520999 MOORLND4 138 1 | 268 | 287 | 0.0402 | 113.98 | System Intact | TDF Impact | Build new MINCO 9 to MINCO 7 765kV Transformer 1
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08729 | 121.73 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08729 | 120.37 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03887 | 107.56 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03345 | 103.53 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.08808 | 102.82 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08729 | 121.73 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08729 | 120.37 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03887 | 107.56 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03345 | 103.53 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR15 | TO->FROM | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.08808 | 102.82 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08835 | 120.32 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08835 | 118.97 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03678 | 114.81 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03274 | 111.55 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08835 | 120.32 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08835 | 118.97 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03678 | 114.81 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03274 | 111.55 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | FROM->TO | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.08835 | 120.32 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.08835 | 118.97 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03678 | 114.81 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR15 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03274 | 111.55 | System Intact | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29WP | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03309 | 151.19 | System Intact | TDF Impact | Woodward - Viola 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR15 | TO->FROM | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 200 | 200 | 0.03439 | 173.32 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Thermal | GEN-2026-PR15 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR15 | TO->FROM | 515785 WINDFRM4 138 520999 MOORLND4 138 1 | 268 | 287 | 0.0402 | 113.98 | System Intact | TDF Impact | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
Non-Converged | GEN-2026-PR15 PSIS CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR15 PSIS CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR15 PSIS CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR15 PSIS CF | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR15 PSIS | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR15 PSIS CF | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on HINTON4 138.0 (511433) 138 kV Bus a. Apply fault at the HINTON4 138.0 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | RHWIND 4 (521117) unit has oscillatory behavior. The reclosing of the line between 511458, and 521116 results in this behavior. Removing the reclosure of the line resolved this issue. This is observed in base case as well requiring the removal of reclosing. | Remove reclosing.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to HAMJCT 2 (511531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 b.2. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to DILL JT2 (520876) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.3. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.4. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCTY-4 (511458) 138.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on ERICK 4 138.00 (520903) 138 kV Bus a. Apply fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | RHWIND 4 (521117) unit has oscillatory behavior. The reclosing of the line between 511458, and 521116 results in this behavior. Removing the reclosure of the line resolved this issue. This is observed in base case as well requiring the removal of reclosing. | Remove reclosing.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on BLKKET TP4 138.00 (511406) 138 kV Bus a. Apply fault at the BLKKET TP4 138.00 (511406) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKKET TP4 (511406) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on CLINTJC2 69.000 (511484) 69 kV Bus a. Apply fault at the CLINTJC2 69.000 (511484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THOMAST2 (511517) 69.0 kV to TREFRY 2 (511518) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on TREFRY 2 69.000 (511518) 69 kV Bus a. Apply fault at the TREFRY 2 69.000 (511518) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TREFRY 2 (511518) 69.0 kV to T CITY 2 (511519) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOSSTAP2 (511522) 69.0 kV to FOSSPLT2 (511523) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WEATHER4 138.00 (511532) 138 kV Bus a. Apply fault at the WEATHER4 138.00 (511532) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on TALBEAR4 138.00 (515460) 138 kV Bus a. Apply fault at the TALBEAR4 138.00 (515460) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CLINTON4 138.00 (520856) 138 kV Bus a. Apply fault at the CLINTON4 138.00 (520856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTON4 (520856) 138.0 kV to WEATHFD4 (521092) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on DILL JT2 69.000 (520876) 69 kV Bus a. Apply fault at the DILL JT2 69.000 (520876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP (769880) 138.0 kV to GEN-2022-145 (769881) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips FRNTWDG1 (515691) and Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability and operational steady state fixes (existing caps/taps/gen set points) for voltage protection trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 1 cycle and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.4. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.5. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply Fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.5. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HINTON4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.3. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHITA2 (521088) 69.0 kV to WASHITA4 (521089) 138.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WEATHER2 69.000 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 b.2. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 b.2. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 b.2. WTH_SE 2 (511496) 69.0 kV to WTH_SE 4 (511497) 138.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on THOMAST2 69.000 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 b.2. THOMAST2 (511517) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to CLINTJC2 (511484) 69.0 kV Transmission Circuit #1 b.2. FOSSTAP2 (511522) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-NGTP4 (511534) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 b.2. WEATHTP4 (511536) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to HINTON 4 (511433) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HINTON 4 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WEATHER2 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLINTJC4 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WTH_SE 2 (511496) 69 kV Bus a. Apply Fault at the WTH_SE 2 (511496) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WTH_SE 4 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WTH WF 4 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on THOMAST2 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on TREFRY 2 (511518) 69 kV Bus a. Apply Fault at the TREFRY 2 (511518) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREFRY 2 (511518) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on T CITY 2 (511519) 69 kV Bus a. Apply Fault at the T CITY 2 (511519) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T CITY 2 (511519) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FOSSTAP2 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WEATHER4 (511532) 138 kV Bus a. Apply Fault at the WEATHER4 (511532) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER4 (511532) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on CLIN-NG4 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on CL-NGTP4 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WEATHTP4 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-145GEN1 (769884) - instant, G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753). Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability. Operational steady state fixes (existing caps/taps/gen set points) for the voltage trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PALDRWG1 (515905) - instant trip, G24-154GEN1 (781594) | Protection disabled with no impact on stability and operational steady state fixes (existing caps/taps/gen set points) for G24-154.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Real power oscillations observed at MORLND2 (520997), and MORLND2 (520997). Voltage protection trips G24-154GEN1 (781594). | Operational steady state fixes (existing caps/taps/gen set points) addressed all the observed issues in violation summary.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PRSMNG11 (515955), G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Real power oscillations observed at MORLND2 (520997), and MORLND2 (520997). Voltage protection trips G24-154GEN1 (781594). | Operational steady state fixes (existing caps/taps/gen set points) addressed all the observed issues in violation summary.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753). Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability. Operational steady state fixes (existing caps/taps/gen set points) for the voltage trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111GEN1 (769204) - instant, G24-154GEN1 (781594) and frequency protection trips G22-111GEN2 (769206) | Protection disabled with no impact on stability and operational steady state fixes (existing caps/taps/gen set points) for G24-154.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753). Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability. Operational steady state fixes (existing caps/taps/gen set points) for the voltage trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111GEN1 (769204) - instant, G24-154GEN1 (781594) and frequency protection trips G22-111GEN2 (769206) | Protection disabled with no impact on stability and operational steady state fixes (existing caps/taps/gen set points) for G24-154.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.7. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on HINTON4 138.0 (511433) 138 kV Bus a. Apply fault at the HINTON4 138.0 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to HAMJCT 2 (511531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 b.2. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to DILL JT2 (520876) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.3. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.4. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCTY-4 (511458) 138.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on ERICK 4 138.00 (520903) 138 kV Bus a. Apply fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on BLKKET TP4 138.00 (511406) 138 kV Bus a. Apply fault at the BLKKET TP4 138.00 (511406) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKKET TP4 (511406) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on CLINTJC2 69.000 (511484) 69 kV Bus a. Apply fault at the CLINTJC2 69.000 (511484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THOMAST2 (511517) 69.0 kV to TREFRY 2 (511518) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on TREFRY 2 69.000 (511518) 69 kV Bus a. Apply fault at the TREFRY 2 69.000 (511518) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TREFRY 2 (511518) 69.0 kV to T CITY 2 (511519) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOSSTAP2 (511522) 69.0 kV to FOSSPLT2 (511523) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WEATHER4 138.00 (511532) 138 kV Bus a. Apply fault at the WEATHER4 138.00 (511532) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on TALBEAR4 138.00 (515460) 138 kV Bus a. Apply fault at the TALBEAR4 138.00 (515460) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CLINTON4 138.00 (520856) 138 kV Bus a. Apply fault at the CLINTON4 138.00 (520856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTON4 (520856) 138.0 kV to WEATHFD4 (521092) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on DILL JT2 69.000 (520876) 69 kV Bus a. Apply fault at the DILL JT2 69.000 (520876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP (769880) 138.0 kV to GEN-2022-145 (769881) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 3.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PALDRWG1 (515905) - instant trip | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 3 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.4. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.5. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply Fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.5. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HINTON4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.3. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHITA2 (521088) 69.0 kV to WASHITA4 (521089) 138.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WEATHER2 69.000 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 b.2. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 b.2. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 b.2. WTH_SE 2 (511496) 69.0 kV to WTH_SE 4 (511497) 138.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on THOMAST2 69.000 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 b.2. THOMAST2 (511517) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to CLINTJC2 (511484) 69.0 kV Transmission Circuit #1 b.2. FOSSTAP2 (511522) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-NGTP4 (511534) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 b.2. WEATHTP4 (511536) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to HINTON 4 (511433) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HINTON 4 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WEATHER2 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLINTJC4 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WTH_SE 2 (511496) 69 kV Bus a. Apply Fault at the WTH_SE 2 (511496) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WTH_SE 4 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WTH WF 4 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on THOMAST2 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on TREFRY 2 (511518) 69 kV Bus a. Apply Fault at the TREFRY 2 (511518) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREFRY 2 (511518) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on T CITY 2 (511519) 69 kV Bus a. Apply Fault at the T CITY 2 (511519) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T CITY 2 (511519) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FOSSTAP2 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WEATHER4 (511532) 138 kV Bus a. Apply Fault at the WEATHER4 (511532) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER4 (511532) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on CLIN-NG4 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on CL-NGTP4 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WEATHTP4 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753). Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability. Operational steady state fixes (existing caps/taps/gen set points) for the voltage trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PALDRWG1 (515905) - instant trip, G24-154GEN1 (781594) | Protection disabled with no impact on stability and operational steady state fixes (existing caps/taps/gen set points) for G24-154.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753). Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability. Operational steady state fixes (existing caps/taps/gen set points) for the voltage trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753). Voltage protection trips G24-154GEN1 (781594) | Protection disabled with no impact on stability. Operational steady state fixes (existing caps/taps/gen set points) for the voltage trip.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167), G23-059GEN3 (773166), and G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Increase acceleration factor to 0.9 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PALDRWG1 (515905) - instant trip, G24-154GEN1 (781594) | Protection disabled with no impact on stability and operational steady state fixes (existing caps/taps/gen set points) for G24-154.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-154GEN1 (781594) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. After acceleration factor adjustment, the event was successfully simulated followed by voltage protection trip for G24-154GEN1 (781594) | Decrease acceleration factor to 0.3 and operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on HINTON4 138.0 (511433) 138 kV Bus a. Apply fault at the HINTON4 138.0 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to HAMJCT 2 (511531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 b.2. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to DILL JT2 (520876) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.3. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.4. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCTY-4 (511458) 138.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on ERICK 4 138.00 (520903) 138 kV Bus a. Apply fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on BLKKET TP4 138.00 (511406) 138 kV Bus a. Apply fault at the BLKKET TP4 138.00 (511406) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKKET TP4 (511406) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on CLINTJC2 69.000 (511484) 69 kV Bus a. Apply fault at the CLINTJC2 69.000 (511484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THOMAST2 (511517) 69.0 kV to TREFRY 2 (511518) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on TREFRY 2 69.000 (511518) 69 kV Bus a. Apply fault at the TREFRY 2 69.000 (511518) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TREFRY 2 (511518) 69.0 kV to T CITY 2 (511519) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOSSTAP2 (511522) 69.0 kV to FOSSPLT2 (511523) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WEATHER4 138.00 (511532) 138 kV Bus a. Apply fault at the WEATHER4 138.00 (511532) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on TALBEAR4 138.00 (515460) 138 kV Bus a. Apply fault at the TALBEAR4 138.00 (515460) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CLINTON4 138.00 (520856) 138 kV Bus a. Apply fault at the CLINTON4 138.00 (520856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTON4 (520856) 138.0 kV to WEATHFD4 (521092) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on DILL JT2 69.000 (520876) 69 kV Bus a. Apply fault at the DILL JT2 69.000 (520876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP (769880) 138.0 kV to GEN-2022-145 (769881) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.4. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.5. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply Fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.5. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HINTON4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.3. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHITA2 (521088) 69.0 kV to WASHITA4 (521089) 138.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WEATHER2 69.000 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 b.2. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 b.2. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 b.2. WTH_SE 2 (511496) 69.0 kV to WTH_SE 4 (511497) 138.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on THOMAST2 69.000 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 b.2. THOMAST2 (511517) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to CLINTJC2 (511484) 69.0 kV Transmission Circuit #1 b.2. FOSSTAP2 (511522) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-NGTP4 (511534) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 b.2. WEATHTP4 (511536) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to HINTON 4 (511433) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HINTON 4 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WEATHER2 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLINTJC4 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WTH_SE 2 (511496) 69 kV Bus a. Apply Fault at the WTH_SE 2 (511496) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WTH_SE 4 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WTH WF 4 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on THOMAST2 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on TREFRY 2 (511518) 69 kV Bus a. Apply Fault at the TREFRY 2 (511518) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREFRY 2 (511518) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on T CITY 2 (511519) 69 kV Bus a. Apply Fault at the T CITY 2 (511519) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T CITY 2 (511519) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FOSSTAP2 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WEATHER4 (511532) 138 kV Bus a. Apply Fault at the WEATHER4 (511532) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER4 (511532) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on CLIN-NG4 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on CL-NGTP4 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WEATHTP4 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on HINTON4 138.0 (511433) 138 kV Bus a. Apply fault at the HINTON4 138.0 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to HAMJCT 2 (511531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 b.2. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to DILL JT2 (520876) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.3. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 b.4. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCTY-4 (511458) 138.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on ERICK 4 138.00 (520903) 138 kV Bus a. Apply fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on CARTERJ2 69.000 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 69.000 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 (520846) 69.0 kV to LKCREEK2 (520978) 69.0 kV Transmission Circuit #1 b.2. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on ONEY 4 138.00 (521017) 138 kV Bus a. Apply fault at the ONEY 4 138.00 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on BLKKET TP4 138.00 (511406) 138 kV Bus a. Apply fault at the BLKKET TP4 138.00 (511406) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKKET TP4 (511406) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on HINTON 4 138.00 (511433) 138 kV Bus a. Apply fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CL-AFTP4 138.00 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 138.00 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on CL-CITY2 69.000 (511447) 69 kV Bus a. Apply fault at the CL-CITY2 69.000 (511447) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-CITY2 (511447) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on CLINTJC2 69.000 (511484) 69 kV Bus a. Apply fault at the CLINTJC2 69.000 (511484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC2 (511484) 69.0 kV to FOSSTAP2 (511522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on THOMAST2 69.000 (511517) 69 kV Bus a. Apply fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THOMAST2 (511517) 69.0 kV to TREFRY 2 (511518) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on TREFRY 2 69.000 (511518) 69 kV Bus a. Apply fault at the TREFRY 2 69.000 (511518) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TREFRY 2 (511518) 69.0 kV to T CITY 2 (511519) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOSSTAP2 (511522) 69.0 kV to FOSSPLT2 (511523) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WEATHER4 138.00 (511532) 138 kV Bus a. Apply fault at the WEATHER4 138.00 (511532) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on TALBEAR4 138.00 (515460) 138 kV Bus a. Apply fault at the TALBEAR4 138.00 (515460) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CLINTON4 138.00 (520856) 138 kV Bus a. Apply fault at the CLINTON4 138.00 (520856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTON4 (520856) 138.0 kV to WEATHFD4 (521092) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on DILL JT2 69.000 (520876) 69 kV Bus a. Apply fault at the DILL JT2 69.000 (520876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILL JT2 (520876) 69.0 kV to ELKCITY2 (520897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-145-TAP (769880) 138.0 kV to GEN-2022-145 (769881) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-145GEN1 (769884) instant trip | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ELKCTY-2 69.000 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 69.000 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 (511459) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on WEATHER2 69.000 (511481) 69 kV Bus a. Apply fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHER2 (511481) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.4. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.5. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply Fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.5. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on REDROCKRD4 138.00 (511548) 138 kV Bus a. Apply Fault at the REDROCKRD4 138.00 (511548) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HINTON4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.3. CL-AFTP4 (511446) 138.0 kV to HOB-JCT4 (511463) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC2 (511484) 69.0 kV to CLINTJC4 (511485) 138.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 b.4. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHITA2 (521088) 69.0 kV to WASHITA4 (521089) 138.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CLIN-NG4 138.00 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 138.00 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. CLINTJC4 (511485) 138.0 kV to CLINTJC2 (511484) 69.0 kV to CLINT1-1 (511499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.3. CLIN-NG4 (511533) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply Fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-AFTP4 (511446) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. ELKCTY-4 (511458) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.3. ELKCTY-4 (511458) 138.0 kV to FALCNRD4 (511511) 138.0 kV Transmission Circuit #1 b.4. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 b.5. ELKCTY-4 (511458) 138.0 kV to ELKCITY6 (511490) 230.0 kV to ELKC2-1 (511482) 13.8 kV Three Winding #1 b.6. ELKCTY-4 (511458) 138.0 kV to ELKCTY-2 (511459) 69.0 kV to ELKC4-1 (511493) 13.8 kV Three Winding #1 b.7. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH WF 4 (511506) 138.0 kV to WEATHERFO_HV (911506) 138.0 kV Transmission Circuit #1 b.4. WTH WF 4 (511506) 138.0 kV to WASHITA (511950) 34.5 kV to WTFWFT1 (511551) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.3. WEATHER4 (511532) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HINTON 4 138.00 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 138.00 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. HINTON 4 (511433) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WEATHER2 69.000 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 69.000 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to WTH_SE 2 (511496) 69.0 kV Transmission Circuit #1 b.2. WEATHER2 (511481) 69.0 kV to THOMAST2 (511517) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to ELKCTY-4 (511458) 138.0 kV Transmission Circuit #1 b.2. CLINTJC4 (511485) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WTH_JCT4 138.00 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 138.00 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to G22-145-TAP (769880) 138.0 kV Transmission Circuit #1 b.2. WTH_JCT4 (511489) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 b.2. WTH_SE 2 (511496) 69.0 kV to WTH_SE 4 (511497) 138.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WTH_SE 4 138.00 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 138.00 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 b.2. WTH_SE 4 (511497) 138.0 kV to WTH_SE 2 (511496) 69.0 kV to WTH_SE-1 (511505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WTH WF 4 138.00 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 138.00 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to CL-NGTP4 (511534) 138.0 kV Transmission Circuit #1 b.2. WTH WF 4 (511506) 138.0 kV to WEATHTP4 (511536) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on THOMAST2 69.000 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 69.000 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 b.2. THOMAST2 (511517) 69.0 kV to WEATHER2 (511481) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FOSSTAP2 69.000 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 69.000 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to CLINTJC2 (511484) 69.0 kV Transmission Circuit #1 b.2. FOSSTAP2 (511522) 69.0 kV to CL-CITY2 (511447) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CL-NGTP4 138.00 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 138.00 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to CLINTJC4 (511485) 138.0 kV Transmission Circuit #1 b.2. CL-NGTP4 (511534) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WEATHTP4 138.00 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 138.00 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to WTH WF 4 (511506) 138.0 kV Transmission Circuit #1 b.2. WEATHTP4 (511536) 138.0 kV to WTH_SE 4 (511497) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on G22-145-TAP 138.00 (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP 138.00 (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to WTH_JCT4 (511489) 138.0 kV Transmission Circuit #1 b.2. G22-145-TAP (769880) 138.0 kV to HINTON 4 (511433) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HINTON 4 (511433) 138 kV Bus a. Apply Fault at the HINTON 4 (511433) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HINTON 4 (511433) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WEATHER2 (511481) 69 kV Bus a. Apply Fault at the WEATHER2 (511481) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER2 (511481) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLINTJC4 (511485) 138 kV Bus a. Apply Fault at the CLINTJC4 (511485) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on WTH_JCT4 (511489) 138 kV Bus a. Apply Fault at the WTH_JCT4 (511489) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_JCT4 (511489) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WTH_SE 2 (511496) 69 kV Bus a. Apply Fault at the WTH_SE 2 (511496) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 2 (511496) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WTH_SE 4 (511497) 138 kV Bus a. Apply Fault at the WTH_SE 4 (511497) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH_SE 4 (511497) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WTH WF 4 (511506) 138 kV Bus a. Apply Fault at the WTH WF 4 (511506) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTH WF 4 (511506) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on THOMAST2 (511517) 69 kV Bus a. Apply Fault at the THOMAST2 (511517) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THOMAST2 (511517) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on TREFRY 2 (511518) 69 kV Bus a. Apply Fault at the TREFRY 2 (511518) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREFRY 2 (511518) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on T CITY 2 (511519) 69 kV Bus a. Apply Fault at the T CITY 2 (511519) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T CITY 2 (511519) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FOSSTAP2 (511522) 69 kV Bus a. Apply Fault at the FOSSTAP2 (511522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOSSTAP2 (511522) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WEATHER4 (511532) 138 kV Bus a. Apply Fault at the WEATHER4 (511532) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHER4 (511532) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on CLIN-NG4 (511533) 138 kV Bus a. Apply Fault at the CLIN-NG4 (511533) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLIN-NG4 (511533) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on CL-NGTP4 (511534) 138 kV Bus a. Apply Fault at the CL-NGTP4 (511534) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CL-NGTP4 (511534) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WEATHTP4 (511536) 138 kV Bus a. Apply Fault at the WEATHTP4 (511536) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHTP4 (511536) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-145GEN1 (769884) instant trip | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on G22-145-TAP (769880) 138 kV Bus a. Apply Fault at the G22-145-TAP (769880) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-145-TAP (769880) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | RHWIND 4 (521117) unit has oscillatory behavior. The reclosing of the line between 511458, and 521116 results in this behavior. Removing the reclosure of the line resolved this issue. This is observed in base case as well requiring the removal of reclosing. | Remove reclosing.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ELKCTY-4 138.00 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 138.00 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 (511458) 138.0 kV to REDHLSW4 (521116) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | RHWIND 4 (521117) unit has oscillatory behavior. The reclosing of the line between 511458, and 521116 results in this behavior. Removing the reclosure of the line resolved this issue. This is observed in base case as well requiring the removal of reclosing. | Remove reclosing.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 1 cycle and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29S | Base | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 3.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 3 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 | 29W | Base | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR15 CF | 29S | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case requiring the same clearing time for resolution. CQ unit was not found to impact the issue. | Clearing time was reduced to 2.5 cycles and issue is resolved.

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR15 | 04 SOUTHEAST | 911506 | WEATHERFO_HV138.00 | 138 | 5.1287 | 5.2975 | 0.1688
GEN-2026-PR15 | 04 SOUTHEAST | 511536 | WEATHTP4 138.00 | 138 | 5.8041 | 5.9423 | 0.1382
GEN-2026-PR15 | 04 SOUTHEAST | 511534 | CL-NGTP4 138.00 | 138 | 6.1193 | 6.2474 | 0.1281
GEN-2026-PR15 | 04 SOUTHEAST | 511533 | CLIN-NG4 138.00 | 138 | 5.9432 | 6.0642 | 0.121
GEN-2026-PR15 | 04 SOUTHEAST | 511497 | WTH_SE 4 138.00 | 138 | 5.6776 | 5.793 | 0.1154
GEN-2026-PR15 | 04 SOUTHEAST | 511489 | WTH_JCT4 138.00 | 138 | 5.6302 | 5.7398 | 0.1096
GEN-2026-PR15 | 04 SOUTHEAST | 511532 | WEATHER4 138.00 | 138 | 5.111 | 5.2193 | 0.1083
GEN-2026-PR15 | 04 SOUTHEAST | 769880 | G22-145-TAP 138.00 | 138 | 5.6103 | 5.7174 | 0.1071
GEN-2026-PR15 | 04 SOUTHEAST | 769881 | GEN-2022-145138.00 | 138 | 5.3449 | 5.4431 | 0.0982
GEN-2026-PR15 | 04 SOUTHEAST | 511485 | CLINTJC4 138.00 | 138 | 6.968 | 7.0591 | 0.0911
GEN-2026-PR15 | 04 SOUTHEAST | 511496 | WTH_SE 2 69.000 | 69 | 5.2387 | 5.2869 | 0.0482
GEN-2026-PR15 | 04 SOUTHEAST | 520856 | CLINTON4 138.00 | 138 | 5.4417 | 5.4867 | 0.045
GEN-2026-PR15 | 04 SOUTHEAST | 511484 | CLINTJC2 69.000 | 69 | 6.2602 | 6.3041 | 0.0439
GEN-2026-PR15 | 04 SOUTHEAST | 511433 | HINTON 4 138.00 | 138 | 6.1721 | 6.2142 | 0.0421
GEN-2026-PR15 | 04 SOUTHEAST | 511481 | WEATHER2 69.000 | 69 | 4.8052 | 4.8448 | 0.0396
GEN-2026-PR15 | 04 SOUTHEAST | 511517 | THOMAST2 69.000 | 69 | 4.6117 | 4.6476 | 0.0359
GEN-2026-PR15 | 04 SOUTHEAST | 511522 | FOSSTAP2 69.000 | 69 | 5.1892 | 5.2228 | 0.0336
GEN-2026-PR15 | 04 SOUTHEAST | 511447 | CL-CITY2 69.000 | 69 | 4.7879 | 4.8184 | 0.0305
GEN-2026-PR15 | 04 SOUTHEAST | 511458 | ELKCTY-4 138.00 | 138 | 11.7619 | 11.7894 | 0.0275
GEN-2026-PR15 | 04 SOUTHEAST | 521092 | WEATHFD4 138.00 | 138 | 4.5864 | 4.6073 | 0.0209
GEN-2026-PR15 | 04 SOUTHEAST | 520503 | DEERCR 4 138.00 | 138 | 4.5368 | 4.5528 | 0.016
GEN-2026-PR15 | 04 SOUTHEAST | 511511 | FALCNRD4 138.00 | 138 | 8.0779 | 8.0903 | 0.0124
GEN-2026-PR15 | 04 SOUTHEAST | 511518 | TREFRY 2 69.000 | 69 | 2.0826 | 2.0921 | 0.0095
GEN-2026-PR15 | 04 SOUTHEAST | 511490 | ELKCITY6 230.00 | 230 | 7.5247 | 7.5328 | 0.0081
GEN-2026-PR15 | 04 SOUTHEAST | 521116 | REDHLSW4 138.00 | 138 | 7.3731 | 7.3804 | 0.0073
GEN-2026-PR15 | 04 SOUTHEAST | 511519 | T CITY 2 69.000 | 69 | 1.7495 | 1.7567 | 0.0072
GEN-2026-PR15 | 04 SOUTHEAST | 511523 | FOSSPLT2 69.000 | 69 | 1.9912 | 1.9977 | 0.0065
GEN-2026-PR15 | 04 SOUTHEAST | 511446 | CL-AFTP4 138.00 | 138 | 6.857 | 6.8634 | 0.0064
GEN-2026-PR15 | 04 SOUTHEAST | 511406 | BLKKET TP4 138.00 | 138 | 5.4286 | 5.4339 | 0.0053
GEN-2026-PR15 | 04 SOUTHEAST | 520471 | DOXEY 4 138.00 | 138 | 5.3504 | 5.3555 | 0.0051
GEN-2026-PR15 | 04 SOUTHEAST | 521117 | RHWIND 4 138.00 | 138 | 6.3349 | 6.34 | 0.0051
GEN-2026-PR15 | 04 SOUTHEAST | 511459 | ELKCTY-2 69.000 | 69 | 7.0867 | 7.0909 | 0.0042
GEN-2026-PR15 | 04 SOUTHEAST | 511463 | HOB-JCT4 138.00 | 138 | 7.2489 | 7.253 | 0.0041
GEN-2026-PR15 | 04 SOUTHEAST | 515497 | MATHWSN7 345.00 | 345 | 36.2505 | 36.2544 | 0.0039
GEN-2026-PR15 | 04 SOUTHEAST | 511535 | CLIN-AF4 138.00 | 138 | 5.2889 | 5.2928 | 0.0039
GEN-2026-PR15 | 04 SOUTHEAST | 520459 | CUSTER 4 138.00 | 138 | 5.552 | 5.5554 | 0.0034
GEN-2026-PR15 | 04 SOUTHEAST | 511467 | L.E.S.-4 138.00 | 138 | 26.1294 | 26.1328 | 0.0034
GEN-2026-PR15 | 04 SOUTHEAST | 511557 | CHISHOLM6 230.00 | 230 | 12.0037 | 12.007 | 0.0033
GEN-2026-PR15 | 04 SOUTHEAST | 520897 | ELKCITY2 69.000 | 69 | 6.0243 | 6.0273 | 0.003
GEN-2026-PR15 | 04 SOUTHEAST | 511554 | RKY_RDG4 138.00 | 138 | 5.7121 | 5.7148 | 0.0027
GEN-2026-PR15 | 04 SOUTHEAST | 511468 | L.E.S.-7 345.00 | 345 | 14.8389 | 14.8408 | 0.0019
GEN-2026-PR15 | 04 SOUTHEAST | 511553 | CHISHOLM7 345.00 | 345 | 12.0972 | 12.0991 | 0.0019
GEN-2026-PR15 | 04 SOUTHEAST | 515045 | SEMINOL7 345.00 | 345 | 29.7104 | 29.7123 | 0.0019
GEN-2026-PR15 | 04 SOUTHEAST | 764550 | G20-087-TAP 345.00 | 345 | 14.5275 | 14.5294 | 0.0019
GEN-2026-PR15 | 04 SOUTHEAST | 764555 | GEN-2020-087345.00 | 345 | 14.5177 | 14.5196 | 0.0019
GEN-2026-PR15 | 04 SOUTHEAST | 781591 | GEN-2024-154345.00 | 345 | 12.0564 | 12.0583 | 0.0019
GEN-2026-PR15 | 04 SOUTHEAST | 763318 | GEN-2018-115345.00 | 345 | 14.5488 | 14.5506 | 0.0018
GEN-2026-PR15 | 04 SOUTHEAST | 516059 | BECKHAM7 345.00 | 345 | 12.1392 | 12.141 | 0.0018
GEN-2026-PR15 | 04 SOUTHEAST | 520462 | ASPEN 4 138.00 | 138 | 21.9752 | 21.977 | 0.0018
GEN-2026-PR15 | 04 SOUTHEAST | 520999 | MOORLND4 138.00 | 138 | 22.8837 | 22.8855 | 0.0018
GEN-2026-PR15 | 04 SOUTHEAST | 515785 | WINDFRM4 138.00 | 138 | 22.2348 | 22.2365 | 0.0017
GEN-2026-PR15 | 04 SOUTHEAST | 760938 | G17-171-TAP 345.00 | 345 | 11.9014 | 11.9027 | 0.0013
GEN-2026-PR15 | 04 SOUTHEAST | 520553 | SEILING4 138.00 | 138 | 7.3435 | 7.3448 | 0.0013
GEN-2026-PR15 | 04 SOUTHEAST | 760939 | GEN-2017-171345.00 | 345 | 11.8324 | 11.8337 | 0.0013
GEN-2026-PR15 | 04 SOUTHEAST | 515375 | WWRDEHV7 345.00 | 345 | 22.1125 | 22.1137 | 0.0012
GEN-2026-PR15 | 04 SOUTHEAST | 765530 | GEN-2021-025138.00 | 138 | 17.9372 | 17.9384 | 0.0012
GEN-2026-PR15 | 04 SOUTHEAST | 511587 | MATO 7 345.00 | 345 | 9.6971 | 9.6983 | 0.0012
GEN-2026-PR15 | 04 SOUTHEAST | 511592 | SEVEN7A_HV 345.00 | 345 | 9.2557 | 9.2569 | 0.0012
GEN-2026-PR15 | 04 SOUTHEAST | 511599 | SEVEN7AB2 345.00 | 345 | 9.2557 | 9.2569 | 0.0012
GEN-2026-PR15 | 04 SOUTHEAST | 511608 | SEVEN7AB3 345.00 | 345 | 9.2557 | 9.2569 | 0.0012
GEN-2026-PR15 | 04 SOUTHEAST | 767301 | GEN-2022-016345.00 | 345 | 21.7936 | 21.7947 | 0.0011
GEN-2026-PR15 | 04 SOUTHEAST | 515407 | TATONGA7 345.00 | 345 | 17.9456 | 17.9467 | 0.0011
GEN-2026-PR15 | 04 SOUTHEAST | 767321 | GEN-2022-017345.00 | 345 | 21.4663 | 21.4674 | 0.0011
GEN-2026-PR15 | 04 SOUTHEAST | 515376 | WWRDEHV4 138.00 | 138 | 26.4252 | 26.4263 | 0.0011
GEN-2026-PR15 | 04 SOUTHEAST | 767221 | GEN-2022-012345.00 | 345 | 21.7722 | 21.7733 | 0.0011
GEN-2026-PR15 | 04 SOUTHEAST | 763527 | GEN-2019-012345.00 | 345 | 19.2089 | 19.2098 | 0.0009
GEN-2026-PR15 | 04 SOUTHEAST | 515458 | BORDER 7345.00 | 345 | 9.6744 | 9.6752 | 0.0008
GEN-2026-PR15 | 04 SOUTHEAST | 514785 | WOODWRD4 138.00 | 138 | 20.2279 | 20.2287 | 0.0008
GEN-2026-PR15 | 04 SOUTHEAST | 515425 | WWDPST 4 138.00 | 138 | 20.2368 | 20.2376 | 0.0008
GEN-2026-PR15 | 04 SOUTHEAST | 515585 | MAMTHPW7 345.00 | 345 | 13.927 | 13.9277 | 0.0007
GEN-2026-PR15 | 04 SOUTHEAST | 515875 | REDNGTN7 345.00 | 345 | 17.7794 | 17.7801 | 0.0007
GEN-2026-PR15 | 04 SOUTHEAST | 515877 | REDDIRT7 345.00 | 345 | 17.7749 | 17.7756 | 0.0007
GEN-2026-PR15 | 04 SOUTHEAST | 515448 | CRSRDSW7 345.00 | 345 | 12.4184 | 12.419 | 0.0006
GEN-2026-PR15 | 04 SOUTHEAST | 514796 | IODINE-4 138.00 | 138 | 7.5598 | 7.5604 | 0.0006
GEN-2026-PR15 | 04 SOUTHEAST | 515961 | GUTHRIE7 345.00 | 345 | 14.0349 | 14.0354 | 0.0005
GEN-2026-PR15 | 04 SOUTHEAST | 520425 | PIC4 138.00 | 138 | 8.3743 | 8.3748 | 0.0005
GEN-2026-PR15 | 04 SOUTHEAST | 516106 | BOBCAT 7 345.00 | 345 | 15.4593 | 15.4597 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 516146 | 25MILE 7 345.00 | 345 | 15.4313 | 15.4317 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 516159 | 25MILZ 7 345.00 | 345 | 15.4041 | 15.4045 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 516036 | TRAV3WD7 345.00 | 345 | 7.1143 | 7.1147 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 514715 | WOODRNG7 345.00 | 345 | 19.1541 | 19.1545 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 515951 | PERSIMN7 345.00 | 345 | 12.2956 | 12.296 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 516192 | WAGNWTIE7 345.00 | 345 | 15.2425 | 15.2429 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 516198 | WAGNWL7 345.00 | 345 | 15.2425 | 15.2429 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 516207 | GADWALL7 345.00 | 345 | 15.2425 | 15.2429 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 762592 | GEN-2018-024345.00 | 345 | 19.1569 | 19.1573 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 914720 | SKELETON__HV345.00 | 345 | 18.1519 | 18.1523 | 0.0004
GEN-2026-PR15 | 04 SOUTHEAST | 515224 | MUSKOGE7 345.00 | 345 | 32.6343 | 32.6346 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 588810 | GEN-2017-040345.00 | 345 | 19.3211 | 19.3214 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 515825 | GRTWSRN7 345.00 | 345 | 10.2949 | 10.2952 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 515786 | FPLWIND4 138.00 | 138 | 6.4977 | 6.498 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 516087 | TRAV22Z7 345.00 | 345 | 5.4052 | 5.4055 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 516109 | TRAV12Z7 345.00 | 345 | 5.0388 | 5.0391 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 521127 | BOILSPR4 138.00 | 138 | 7.9305 | 7.9308 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 511531 | HAMJCT 2 69.000 | 69 | 1.7823 | 1.7826 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 509782 | R.S.S.-7 345.00 | 345 | 31.8672 | 31.8675 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 511877 | G16133G16146345.00 | 345 | 31.8672 | 31.8675 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 514714 | WOODRNG4 138.00 | 138 | 20.1294 | 20.1297 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 514803 | SOONER 7 345.00 | 345 | 28.0395 | 28.0398 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 515422 | C-RIVER7 345.00 | 345 | 11.6926 | 11.6929 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 515582 | SLNGWND7 345.00 | 345 | 8.7066 | 8.7069 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 516086 | TRAV3WZ7 345.00 | 345 | 6.6396 | 6.6399 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 516091 | OKTAHA 7 345.00 | 345 | 17.7465 | 17.7468 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 516210 | RAVEN 7 345.00 | 345 | 19.7927 | 19.793 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 520957 | IODINE 4 138.00 | 138 | 8.1479 | 8.1482 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 520995 | MOORLND2 69.000 | 69 | 8.888 | 8.8883 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 562020 | PRSCRKII 7 345.00 | 345 | 11.1941 | 11.1944 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 588838 | G17-092-SWYD345.00 | 345 | 19.7927 | 19.793 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 776060 | G23-204-TAP 345.00 | 345 | 17.3045 | 17.3048 | 0.0003
GEN-2026-PR15 | 04 SOUTHEAST | 508359 | WELSH 7 345.00 | 345 | 22.8163 | 22.8165 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 508831 | DIANA 4 138.00 | 138 | 28.453 | 28.4532 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 508847 | WELSHDC1 345.00 | 345 | 21.9553 | 21.9555 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 508848 | SPPMAINBUS 345.00 | 345 | 21.9553 | 21.9555 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 509834 | COGENT 7 345.00 | 345 | 29.4673 | 29.4675 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 515778 | GRIFFIN7 345.00 | 345 | 23.3097 | 23.3099 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 776061 | GEN-2023-204345.00 | 345 | 17.2897 | 17.2899 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 762321 | GEN-2017-164345.00 | 345 | 11.4309 | 11.4311 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 516108 | TRAV11Z7 345.00 | 345 | 5.039 | 5.0392 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 508562 | PIRKEY 4 138.00 | 138 | 32.0338 | 32.034 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 515235 | PECANCK7 345.00 | 345 | 24.3272 | 24.3274 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 515300 | FTSMTHE5 161.00 | 161 | 25.3568 | 25.357 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 515301 | FTSMTHW5 161.00 | 161 | 25.2225 | 25.2227 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 515394 | KEENAN 4 138.00 | 138 | 9.0691 | 9.0693 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 516010 | PINTAIL7 345.00 | 345 | 16.4451 | 16.4453 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 516019 | KINGWD 7 345.00 | 345 | 16.3861 | 16.3863 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 516045 | TRAV2WD7 345.00 | 345 | 5.7032 | 5.7034 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 516054 | TRAV1WD7 345.00 | 345 | 5.2942 | 5.2944 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 516107 | TRAV21Z7 345.00 | 345 | 5.4052 | 5.4054 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 585420 | SUBST HS 345.00 | 345 | 7.9361 | 7.9363 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 588560 | GEN-2017-011345.00 | 345 | 12.4474 | 12.4476 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 589300 | GEN-2017-092345.00 | 345 | 15.9162 | 15.9164 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 765660 | GEN-2021-038345.00 | 345 | 21.1451 | 21.1453 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 508072 | NWTXARK7 345.00 | 345 | 14.3381 | 14.3383 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 508840 | WILKES 4 138.00 | 138 | 29.8149 | 29.8151 | 0.0002
GEN-2026-PR15 | 04 SOUTHEAST | 507774 | NORAM 4 138.00 | 138 | 16.4018 | 16.4019 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 508861 | AVINGTP4 138.00 | 138 | 18.4181 | 18.4182 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 509745 | CLARKSV7 345.00 | 345 | 20.9658 | 20.9659 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 515234 | PECANCK5 161.00 | 161 | 21.1793 | 21.1794 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 515299 | BEVYTAP5 161.00 | 161 | 22.1283 | 22.1284 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 338807 | 5NUC-YAM-S# 161.00 | 161 | 9.7634 | 9.7635 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 507760 | SW SHV 7 345.00 | 345 | 14.6031 | 14.6032 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 508563 | PIRKEY 7 345.00 | 345 | 15.5276 | 15.5277 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 508567 | SCOTTSV4 138.00 | 138 | 11.2788 | 11.2789 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 508833 | IPCJEFF4 138.00 | 138 | 12.4494 | 12.4495 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 509639 | DIANASW4 138.00 | 138 | 11.995 | 11.9951 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 765480 | GEN-2021-019345.00 | 345 | 12.6906 | 12.6907 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 769201 | GEN-2022-111345.00 | 345 | 15.1221 | 15.1222 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 509624 | LAKEPIN4 138.00 | 138 | 7.5192 | 7.5193 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 509628 | NOONDAY4 138.00 | 138 | 5.832 | 5.8321 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7345.00 | 345 | 5.266 | 5.2661 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 511726 | ZONE-5 SUB 345.00 | 345 | 6.771 | 6.7711 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 511880 | G16133_765R2765.00 | 765 | 4.2734 | 4.2735 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 512759 | WAGCTY22 69.000 | 69 | 5.571 | 5.5711 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 914715 | SKELETON__HV345.00 | 345 | 5.81 | 5.8101 | 0.0001
GEN-2026-PR15 | 04 SOUTHEAST | 511999 | DVRSION-WIND345.00 | 345 | 3.6808 | 3.6809 | 0.0001

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR15 | 2.1406 | FAIL | 0.36824 | PASS | N/A | N/A | Yes

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | BASE CASE | 6.7378 | PASS | 0.39065 | PASS | 290.6504 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 6.7378 | PASS | 0.39065 | PASS | 290.6507 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511406 [BLKKET TP4 138.00] TO BUS 511504 [SAYRE--4 138.00] CKT 1 | 6.7265 | PASS | 0.39071 | PASS | 290.7149 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511406 [BLKKET TP4 138.00] TO BUS 511511 [FALCNRD4 138.00] CKT 1 | 6.7263 | PASS | 0.39072 | PASS | 290.7158 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511406 [BLKKET TP4 138.00] TO BUS 520471 [DOXEY 4 138.00] CKT 1 | 6.7378 | PASS | 0.39065 | PASS | 290.6511 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 6.7331 | PASS | 0.39067 | PASS | 290.6705 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511444 [ROSVTAP2 69.00] TO BUS 511465 [HOBART-2 69.00] CKT 1 | 6.7322 | PASS | 0.39066 | PASS | 290.6629 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 6.6871 | PASS | 0.39069 | PASS | 290.6919 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 6.6953 | PASS | 0.39068 | PASS | 290.6751 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 765890 [GEN-2021-064 138.00] CKT 1 | 6.7394 | PASS | 0.39065 | PASS | 290.6463 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511446 [CL-AFTP4 138.00] TO BUS 511458 [ELKCTY-4 138.00] CKT 1 | 6.5902 | PASS | 0.39103 | PASS | 291.0317 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511446 [CL-AFTP4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 6.5902 | PASS | 0.39102 | PASS | 291.0227 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511446 [CL-AFTP4 138.00] TO BUS 511535 [CLIN-AF4 138.00] CKT 1 | 6.7379 | PASS | 0.39065 | PASS | 290.6546 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511447 [CL-CITY2 69.00] TO BUS 511517 [THOMAST2 69.00] CKT 1 | 6.6896 | PASS | 0.39078 | PASS | 290.7837 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511447 [CL-CITY2 69.00] TO BUS 511522 [FOSSTAP2 69.00] CKT 1 | 6.696 | PASS | 0.39145 | PASS | 291.4501 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511485 [CLINTJC4 138.00] CKT 1 | 4.2179 | PASS | 0.40264 | PASS | 302.6426 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511511 [FALCNRD4 138.00] CKT 1 | 6.729 | PASS | 0.39073 | PASS | 290.7251 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 521116 [REDHLSW4 138.00] CKT 1 | 6.6403 | PASS | 0.39111 | PASS | 291.1108 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511459 [ELKCTY-2 69.00] TO BUS 511531 [HAMJCT 2 69.00] CKT 1 | 6.7375 | PASS | 0.39065 | PASS | 290.6532 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511459 [ELKCTY-2 69.00] TO BUS 520897 [ELKCITY2 69.00] CKT 1 | 6.7103 | PASS | 0.39077 | PASS | 290.7705 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511463 [HOB-JCT4 138.00] TO BUS 511554 [RKY_RDG4 138.00] CKT 1 | 6.7373 | PASS | 0.39068 | PASS | 290.6754 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511463 [HOB-JCT4 138.00] TO BUS 511564 [MARTHA 4 138.00] CKT 1 | 6.7194 | PASS | 0.39071 | PASS | 290.7081 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511464 [HOB-JCT2 69.00] TO BUS 511465 [HOBART-2 69.00] CKT 1 | 6.7318 | PASS | 0.39067 | PASS | 290.6713 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 6.7328 | PASS | 0.39067 | PASS | 290.6731 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4 138.00] CKT 1 | 6.731 | PASS | 0.39068 | PASS | 290.68 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 6.7332 | PASS | 0.39068 | PASS | 290.6772 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 6.7299 | PASS | 0.39068 | PASS | 290.6761 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 6.6562 | PASS | 0.39111 | PASS | 291.1125 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 776561 [GEN-2023-229 138.00] CKT 1 | 6.7409 | PASS | 0.39071 | PASS | 290.7097 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511481 [WEATHER2 69.00] TO BUS 511496 [WTH_SE 2 69.00] CKT 1 | 6.6836 | PASS | 0.39023 | PASS | 290.2284 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511481 [WEATHER2 69.00] TO BUS 511517 [THOMAST2 69.00] CKT 1 | 6.6884 | PASS | 0.39067 | PASS | 290.6685 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511484 [CLINTJC2 69.00] TO BUS 511522 [FOSSTAP2 69.00] CKT 1 | 6.6961 | PASS | 0.39146 | PASS | 291.462 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511485 [CLINTJC4 138.00] TO BUS 511534 [CL-NGTP4 138.00] CKT 1 | 5.8391 | PASS | 0.37309 | PASS | 273.086 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511485 [CLINTJC4 138.00] TO BUS 520856 [CLINTON4 138.00] CKT 1 | 2.1637 | PASS | 0.59058 | PASS | 490.5771 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511489 [WTH_JCT4 138.00] TO BUS 511497 [WTH_SE 4 138.00] CKT 1 | 5.5574 | PASS | 0.38029 | PASS | 280.2947 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511489 [WTH_JCT4 138.00] TO BUS 769880 [G22-145-TAP 138.00] CKT 1 | 5.5771 | PASS | 0.38081 | PASS | 280.8131 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511490 [ELKCITY6 230.00] TO BUS 511557 [CHISHOLM6 230.00] CKT 1 | 5.9675 | PASS | 0.39229 | PASS | 292.2897 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511497 [WTH_SE 4 138.00] TO BUS 511536 [WEATHTP4 138.00] CKT 1 | 5.9772 | PASS | 0.37776 | PASS | 277.7623 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511504 [SAYRE--4 138.00] TO BUS 520903 [ERICK 4 138.00] CKT 1 | 6.7298 | PASS | 0.3907 | PASS | 290.6977 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511506 [WTH WF 4 138.00] TO BUS 511534 [CL-NGTP4 138.00] CKT 1 | 5.8292 | PASS | 0.36993 | PASS | 269.9266 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511506 [WTH WF 4 138.00] TO BUS 511536 [WEATHTP4 138.00] CKT 1 | 5.9565 | PASS | 0.37709 | PASS | 277.0907 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511517 [THOMAST2 69.00] TO BUS 511518 [TREFRY 2 69.00] CKT 1 | 6.7355 | PASS | 0.39063 | PASS | 290.6322 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511518 [TREFRY 2 69.00] TO BUS 511519 [T CITY 2 69.00] CKT 1 | 6.7354 | PASS | 0.39063 | PASS | 290.6286 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511522 [FOSSTAP2 69.00] TO BUS 511523 [FOSSPLT2 69.00] CKT 1 | 6.7376 | PASS | 0.39065 | PASS | 290.6539 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511532 [WEATHER4 138.00] TO BUS 511536 [WEATHTP4 138.00] CKT 1 | 6.7261 | PASS | 0.39035 | PASS | 290.3512 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511533 [CLIN-NG4 138.00] TO BUS 511534 [CL-NGTP4 138.00] CKT 1 | 6.7199 | PASS | 0.39047 | PASS | 290.4708 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511542 [BUFFCK6 230.00] CKT 1 | 6.7351 | PASS | 0.39066 | PASS | 290.6631 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511544 [DEMPSEYR_HV 230.00] CKT 1 | 6.7318 | PASS | 0.39067 | PASS | 290.6707 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511547 [ROARK6 230.00] CKT 1 | 6.7307 | PASS | 0.39067 | PASS | 290.6704 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511557 [CHISHOLM6 230.00] CKT 1 | 6.7029 | PASS | 0.39078 | PASS | 290.7821 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 6.7115 | PASS | 0.39072 | PASS | 290.7173 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 6.6658 | PASS | 0.39076 | PASS | 290.7638 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 6.6254 | PASS | 0.39085 | PASS | 290.8477 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 781591 [GEN-2024-154 345.00] CKT 1 | 6.7457 | PASS | 0.39064 | PASS | 290.6357 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511561 [ELLIS 4 138.00] TO BUS 520459 [CUSTER 4 138.00] CKT 1 | 6.667 | PASS | 0.39081 | PASS | 290.8126 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511561 [ELLIS 4 138.00] TO BUS 521001 [MORWODS4 138.00] CKT 1 | 6.6717 | PASS | 0.39079 | PASS | 290.7897 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511564 [MARTHA 4 138.00] TO BUS 529302 [OMALTUS4 138.00] CKT 1 | 6.7199 | PASS | 0.39071 | PASS | 290.7056 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 511592 [SEVEN7A_HV 345.00] CKT 1 | 6.7214 | PASS | 0.39068 | PASS | 290.6762 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 6.6958 | PASS | 0.39072 | PASS | 290.7199 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 6.6927 | PASS | 0.39074 | PASS | 290.7368 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 6.736 | PASS | 0.39065 | PASS | 290.6547 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 2 | 6.736 | PASS | 0.39065 | PASS | 290.6547 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 2 | 6.7126 | PASS | 0.39069 | PASS | 290.6905 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520402 [BULOJ4 138.00] TO BUS 520903 [ERICK 4 138.00] CKT 1 | 6.7288 | PASS | 0.39069 | PASS | 290.6906 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520459 [CUSTER 4 138.00] TO BUS 521116 [REDHLSW4 138.00] CKT 1 | 6.6664 | PASS | 0.39082 | PASS | 290.8161 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520468 [HINTON 4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 6.7377 | PASS | 0.39067 | PASS | 290.6693 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520503 [DEERCR 4 138.00] TO BUS 520950 [HYDRO 4 138.00] CKT 1 | 4.7051 | PASS | 0.4094 | PASS | 309.398 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520503 [DEERCR 4 138.00] TO BUS 521092 [WEATHFD4 138.00] CKT 1 | 4.7005 | PASS | 0.41004 | PASS | 310.043 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521010 [NIJECT 4 138.00] CKT 1 | 6.7383 | PASS | 0.39067 | PASS | 290.6743 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 4.7359 | PASS | 0.40542 | PASS | 305.4173 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 4.7282 | PASS | 0.40632 | PASS | 306.3247 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520846 [CARTERJ2 69.00] TO BUS 520876 [DILL JT2 69.00] CKT 1 | 6.7088 | PASS | 0.39074 | PASS | 290.7435 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520846 [CARTERJ2 69.00] TO BUS 520978 [LKCREEK2 69.00] CKT 1 | 6.7089 | PASS | 0.39074 | PASS | 290.7434 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520856 [CLINTON4 138.00] TO BUS 521092 [WEATHFD4 138.00] CKT 1 | 4.6949 | PASS | 0.41091 | PASS | 310.9109 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520873 [CANUTE 2 69.00] TO BUS 520875 [DILL 2 69.00] CKT 1 | 6.738 | PASS | 0.39065 | PASS | 290.6524 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520873 [CANUTE 2 69.00] TO BUS 520876 [DILL JT2 69.00] CKT 1 | 6.7383 | PASS | 0.39065 | PASS | 290.6535 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520876 [DILL JT2 69.00] TO BUS 520897 [ELKCITY2 69.00] CKT 1 | 6.7092 | PASS | 0.39075 | PASS | 290.7493 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520950 [HYDRO 4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 4.7156 | PASS | 0.40795 | PASS | 307.9511 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521001 [MORWODS4 138.00] TO BUS 521002 [MORWOOD4 138.00] CKT 1 | 6.7293 | PASS | 0.39068 | PASS | 290.6778 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521001 [MORWODS4 138.00] TO BUS 521128 [NINMLTP4 138.00] CKT 1 | 6.608 | PASS | 0.39095 | PASS | 290.9535 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 4.7449 | PASS | 0.40442 | PASS | 304.4164 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521116 [REDHLSW4 138.00] TO BUS 521117 [RHWIND 4 138.00] CKT 1 | 6.7138 | PASS | 0.39087 | PASS | 290.875 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 6.7201 | PASS | 0.39069 | PASS | 290.6853 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 529298 [OMPVET-4 138.00] TO BUS 529302 [OMALTUS4 138.00] CKT 1 | 6.7199 | PASS | 0.39069 | PASS | 290.6945 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 6.7332 | PASS | 0.39067 | PASS | 290.6696 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511444 [ROSVTAP2 69.00] TO BUS 511432 [R-AMOCO2 69.00] CKT 1 | 6.7378 | PASS | 0.39065 | PASS | 290.6509 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511444 [ROSVTAP2 69.00] TO BUS 511495 [TOMSTEED2 69.00] CKT 1 | 6.7323 | PASS | 0.39066 | PASS | 290.6621 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511459 [ELKCTY-2 69.00] CKT 1 | 6.7105 | PASS | 0.39078 | PASS | 290.7786 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511490 [ELKCITY6 230.00] CKT 1 | 5.9675 | PASS | 0.39229 | PASS | 292.2897 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511463 [HOB-JCT4 138.00] TO BUS 511464 [HOB-JCT2 69.00] CKT 1 | 6.7318 | PASS | 0.39067 | PASS | 290.6713 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.4.00] CKT 1 | 6.7375 | PASS | 0.39065 | PASS | 290.6513 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.4.00] CKT 1 | 6.7376 | PASS | 0.39065 | PASS | 290.6513 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.00] CKT 1 | 6.7018 | PASS | 0.39072 | PASS | 290.7159 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.8.00] CKT 1 | 6.7306 | PASS | 0.39066 | PASS | 290.6646 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 6.7334 | PASS | 0.39067 | PASS | 290.6692 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511484 [CLINTJC2 69.00] TO BUS 511485 [CLINTJC4 138.00] CKT 1 | 6.6961 | PASS | 0.39146 | PASS | 291.4603 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511496 [WTH_SE 2 69.00] TO BUS 511497 [WTH_SE 4 138.00] CKT 1 | 6.6836 | PASS | 0.39023 | PASS | 290.2286 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511506 [WTH WF 4 138.00] TO BUS 511950 [WASHITA 34.5.00] CKT 1 | 6.7196 | PASS | 0.38733 | PASS | 287.3262 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511542 [BUFFCK6 230.00] TO BUS 511959 [BUFFCK1 34.5.00] CKT 1 | 6.7354 | PASS | 0.39066 | PASS | 290.6623 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511544 [DEMPSEYR_HV 230.00] TO BUS 511961 [DEMPSE34.5_1 34.5.00] CKT 1 | 6.7325 | PASS | 0.39067 | PASS | 290.6693 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511547 [ROARK6 230.00] TO BUS 511960 [ROARK1 34.5.00] CKT 1 | 6.7316 | PASS | 0.39067 | PASS | 290.6686 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511557 [CHISHOLM6 230.00] CKT 1 | 6.3458 | PASS | 0.39123 | PASS | 291.2287 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511554 [RKY_RDG4 138.00] TO BUS 511963 [RKYRDGW1-1 34.5.00] CKT 1 | 6.7374 | PASS | 0.39066 | PASS | 290.6629 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511554 [RKY_RDG4 138.00] TO BUS 511962 [RKYRDGW2-1 34.5.00] CKT 1 | 6.7378 | PASS | 0.39066 | PASS | 290.6618 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511563 [ELSWORTH 4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 6.7312 | PASS | 0.39068 | PASS | 290.6789 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 6.7319 | PASS | 0.39067 | PASS | 290.6726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 6.7389 | PASS | 0.39065 | PASS | 290.6533 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511592 [SEVEN7A_HV 345.00] TO BUS 511599 [SEVEN7AB2 345.00] CKT 1 | 6.7279 | PASS | 0.39067 | PASS | 290.6655 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511592 [SEVEN7A_HV 345.00] TO BUS 511608 [SEVEN7AB3 345.00] CKT 1 | 6.7316 | PASS | 0.39066 | PASS | 290.6606 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 6.7335 | PASS | 0.39066 | PASS | 290.6576 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 6.7334 | PASS | 0.39066 | PASS | 290.6578 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 6.739 | PASS | 0.39065 | PASS | 290.6462 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 6.739 | PASS | 0.39065 | PASS | 290.6462 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 6.7318 | PASS | 0.39066 | PASS | 290.6628 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 6.7356 | PASS | 0.39065 | PASS | 290.6537 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 6.7356 | PASS | 0.39065 | PASS | 290.6537 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 6.735 | PASS | 0.39066 | PASS | 290.6551 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 6.7363 | PASS | 0.39065 | PASS | 290.6529 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 6.7336 | PASS | 0.39066 | PASS | 290.6582 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 2 | 6.7358 | PASS | 0.39065 | PASS | 290.6528 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 3 | 6.7357 | PASS | 0.39065 | PASS | 290.6529 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 525832 [TUCO_INT 7 345.00] CKT 1 | 6.7222 | PASS | 0.39067 | PASS | 290.6715 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 6.7369 | PASS | 0.39066 | PASS | 290.6592 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 6.7086 | PASS | 0.39072 | PASS | 290.7249 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] CKT 3 | 6.7044 | PASS | 0.39078 | PASS | 290.7824 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520402 [BULOJ4 138.00] TO BUS 521060 [SWEETWR4 138.00] CKT 1 | 6.729 | PASS | 0.39069 | PASS | 290.69 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.7351 | PASS | 0.39067 | PASS | 290.6652 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 2 | 6.7365 | PASS | 0.39066 | PASS | 290.6574 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 3 | 6.7365 | PASS | 0.39066 | PASS | 290.6574 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520422 [SEQUOYAHJ4 138.00] CKT 1 | 6.7365 | PASS | 0.39066 | PASS | 290.6578 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520508 [CLVLDSW4 138.00] CKT 1 | 6.7377 | PASS | 0.39064 | PASS | 290.6409 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.8.00] CKT 1 | 6.7327 | PASS | 0.39066 | PASS | 290.6596 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.8.00] CKT 1 | 6.7327 | PASS | 0.39066 | PASS | 290.6595 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.8.00] CKT 1 | 6.7327 | PASS | 0.39066 | PASS | 290.6596 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 6.736 | PASS | 0.39066 | PASS | 290.6593 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 6.7369 | PASS | 0.39066 | PASS | 290.6649 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.8.00] CKT 1 | 6.7355 | PASS | 0.39065 | PASS | 290.6548 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.8.00] CKT 1 | 6.7352 | PASS | 0.39066 | PASS | 290.6553 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.8.00] CKT 1 | 6.7339 | PASS | 0.39066 | PASS | 290.6577 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.8.00] CKT 1 | 6.7339 | PASS | 0.39066 | PASS | 290.6578 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.8.00] CKT 1 | 6.7343 | PASS | 0.39066 | PASS | 290.657 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 6.7372 | PASS | 0.39065 | PASS | 290.652 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520810 [ANADARK2 69.00] CKT 1 | 6.7379 | PASS | 0.39065 | PASS | 290.6501 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520978 [LKCREEK2 69.00] TO BUS 520927 [GRANITE2 69.00] CKT 1 | 6.7273 | PASS | 0.39068 | PASS | 290.6798 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520978 [LKCREEK2 69.00] TO BUS 520982 [LONEWLF2 69.00] CKT 1 | 6.7317 | PASS | 0.39067 | PASS | 290.6703 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521000 [MORWODS2 69.00] TO BUS 520457 [BTLRJCT2 69.00] CKT 1 | 6.7373 | PASS | 0.39066 | PASS | 290.6577 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521000 [MORWODS2 69.00] TO BUS 521001 [MORWODS4 138.00] CKT 1 | 6.7373 | PASS | 0.39066 | PASS | 290.6577 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521002 [MORWOOD4 138.00] TO BUS 520832 [BRANTLEY4 138.00] CKT 1 | 6.729 | PASS | 0.39068 | PASS | 290.6785 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.7165 | PASS | 0.39074 | PASS | 290.7444 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 2 | 6.722 | PASS | 0.39072 | PASS | 290.7201 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 6.7463 | PASS | 0.39069 | PASS | 290.6869 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 521088 [WASHITA2 69.00] CKT 1 | 6.7365 | PASS | 0.39066 | PASS | 290.6601 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521117 [RHWIND 4 138.00] TO BUS 521119 [REDHILLS WF1 34.5.00] CKT 1 | 6.714 | PASS | 0.39087 | PASS | 290.8746 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521128 [NINMLTP4 138.00] TO BUS 520492 [NINMILE4 138.00] CKT 1 | 6.7378 | PASS | 0.39065 | PASS | 290.6504 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521128 [NINMLTP4 138.00] TO BUS 520500 [BEARCAT4 138.00] CKT 1 | 6.6075 | PASS | 0.39095 | PASS | 290.954 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 6.7235 | PASS | 0.39067 | PASS | 290.6673 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523770 [GRAPEVINE 3 115.00] CKT 1 | 6.7373 | PASS | 0.39065 | PASS | 290.6541 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523776 [WHEELER 3 115.00] TO BUS 523772 [COBRN_CREEK3 115.00] CKT 1 | 6.7428 | PASS | 0.39065 | PASS | 290.645 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523776 [WHEELER 3 115.00] TO BUS 523797 [HOWARD 3 115.00] CKT 1 | 6.7354 | PASS | 0.39066 | PASS | 290.659 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523776 [WHEELER 3 115.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 6.7325 | PASS | 0.39067 | PASS | 290.6679 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 6.7154 | PASS | 0.39069 | PASS | 290.6871 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 524296 [SPNSPUR_WND7 345.00] CKT 1 | 6.7307 | PASS | 0.39066 | PASS | 290.6628 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 525549 [TOLK 7 345.00] CKT 1 | 6.7369 | PASS | 0.39065 | PASS | 290.6513 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] CKT 1 | 6.7377 | PASS | 0.39065 | PASS | 290.6506 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] CKT 1 | 6.7377 | PASS | 0.39065 | PASS | 290.6506 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] CKT 1 | 6.7377 | PASS | 0.39065 | PASS | 290.6506 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] CKT 2 | 6.7398 | PASS | 0.39065 | PASS | 290.6464 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] CKT 1 | 6.7386 | PASS | 0.39065 | PASS | 290.6486 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 529298 [OMPVET-4 138.00] TO BUS 529345 [OMPARK-4 138.00] CKT 1 | 6.7195 | PASS | 0.39069 | PASS | 290.688 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 765890 [GEN-2021-064 138.00] TO BUS 765894 [G21-064-XFM1 34.5.00] CKT 1 | 6.7394 | PASS | 0.39065 | PASS | 290.6463 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 769880 [G22-145-TAP 138.00] TO BUS 511433 [HINTON 4 138.00] CKT 1 | 5.4834 | PASS | 0.38106 | PASS | 281.0617 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 769880 [G22-145-TAP 138.00] TO BUS 769881 [GEN-2022-145 138.00] CKT 1 | 6.7642 | PASS | 0.39061 | PASS | 290.6138 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 776561 [GEN-2023-229 138.00] TO BUS 776562 [G23-229XFMR1 34.5.00] CKT 1 | 6.7396 | PASS | 0.39068 | PASS | 290.6786 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 776561 [GEN-2023-229 138.00] TO BUS 776565 [G23-229XFMR2 34.5.00] CKT 1 | 6.7392 | PASS | 0.39068 | PASS | 290.6758 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 781591 [GEN-2024-154 345.00] TO BUS 781592 [G24-154XFMR1 34.5.00] CKT 1 | 6.7457 | PASS | 0.39064 | PASS | 290.6357 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 6.7155 | PASS | 0.39069 | PASS | 290.6856 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 6.7431 | PASS | 0.39063 | PASS | 290.6317 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 6.7086 | PASS | 0.39069 | PASS | 290.6932 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.7316 | PASS | 0.39068 | PASS | 290.6837 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.7316 | PASS | 0.39068 | PASS | 290.6837 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 2 | 6.7343 | PASS | 0.39067 | PASS | 290.6691 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.6625 | PASS | 0.39099 | PASS | 290.9854 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | BASE CASE | 6.6556 | PASS | 0.38927 | PASS | 289.2724 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 6.6555 | PASS | 0.38927 | PASS | 289.2726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511406 [BLKKET TP4 138.00] TO BUS 511504 [SAYRE--4 138.00] CKT 1 | 6.6475 | PASS | 0.38933 | PASS | 289.3272 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511406 [BLKKET TP4 138.00] TO BUS 511511 [FALCNRD4 138.00] CKT 1 | 6.6474 | PASS | 0.38933 | PASS | 289.3273 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511406 [BLKKET TP4 138.00] TO BUS 520471 [DOXEY 4 138.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2734 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 6.6495 | PASS | 0.3893 | PASS | 289.299 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511444 [ROSVTAP2 69.00] TO BUS 511465 [HOBART-2 69.00] CKT 1 | 6.6504 | PASS | 0.38928 | PASS | 289.2838 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 6.6216 | PASS | 0.38929 | PASS | 289.2946 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 6.6212 | PASS | 0.38929 | PASS | 289.2929 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 765890 [GEN-2021-064 138.00] CKT 1 | 6.655 | PASS | 0.38927 | PASS | 289.2722 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511446 [CL-AFTP4 138.00] TO BUS 511458 [ELKCTY-4 138.00] CKT 1 | 6.537 | PASS | 0.38961 | PASS | 289.6116 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511446 [CL-AFTP4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 6.5368 | PASS | 0.38961 | PASS | 289.6072 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511446 [CL-AFTP4 138.00] TO BUS 511535 [CLIN-AF4 138.00] CKT 1 | 6.6555 | PASS | 0.38928 | PASS | 289.2757 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511447 [CL-CITY2 69.00] TO BUS 511517 [THOMAST2 69.00] CKT 1 | 6.6126 | PASS | 0.38941 | PASS | 289.4069 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511447 [CL-CITY2 69.00] TO BUS 511522 [FOSSTAP2 69.00] CKT 1 | 6.6148 | PASS | 0.38982 | PASS | 289.8225 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511485 [CLINTJC4 138.00] CKT 1 | 4.1059 | PASS | 0.40193 | PASS | 301.9304 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511511 [FALCNRD4 138.00] CKT 1 | 6.6488 | PASS | 0.38934 | PASS | 289.3376 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 521116 [REDHLSW4 138.00] CKT 1 | 6.5811 | PASS | 0.38971 | PASS | 289.7095 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511459 [ELKCTY-2 69.00] TO BUS 511531 [HAMJCT 2 69.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.273 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511459 [ELKCTY-2 69.00] TO BUS 520897 [ELKCITY2 69.00] CKT 1 | 6.6327 | PASS | 0.38939 | PASS | 289.3945 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511463 [HOB-JCT4 138.00] TO BUS 511554 [RKY_RDG4 138.00] CKT 1 | 6.6573 | PASS | 0.3893 | PASS | 289.3033 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511463 [HOB-JCT4 138.00] TO BUS 511564 [MARTHA 4 138.00] CKT 1 | 6.6366 | PASS | 0.38933 | PASS | 289.3298 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511464 [HOB-JCT2 69.00] TO BUS 511465 [HOBART-2 69.00] CKT 1 | 6.6499 | PASS | 0.38929 | PASS | 289.2899 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 6.6487 | PASS | 0.3893 | PASS | 289.303 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4 138.00] CKT 1 | 6.6445 | PASS | 0.38931 | PASS | 289.3134 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 6.6455 | PASS | 0.38931 | PASS | 289.3132 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 6.6402 | PASS | 0.38931 | PASS | 289.309 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 6.6052 | PASS | 0.38969 | PASS | 289.6909 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 776561 [GEN-2023-229 138.00] CKT 1 | 6.6559 | PASS | 0.38938 | PASS | 289.3754 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511481 [WEATHER2 69.00] TO BUS 511496 [WTH_SE 2 69.00] CKT 1 | 6.6138 | PASS | 0.38909 | PASS | 289.0939 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511481 [WEATHER2 69.00] TO BUS 511517 [THOMAST2 69.00] CKT 1 | 6.612 | PASS | 0.38934 | PASS | 289.3393 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511484 [CLINTJC2 69.00] TO BUS 511522 [FOSSTAP2 69.00] CKT 1 | 6.6149 | PASS | 0.38983 | PASS | 289.8266 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511485 [CLINTJC4 138.00] TO BUS 511534 [CL-NGTP4 138.00] CKT 1 | 5.8247 | PASS | 0.37138 | PASS | 271.3832 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511485 [CLINTJC4 138.00] TO BUS 520856 [CLINTON4 138.00] CKT 1 | 2.1406 | PASS | 0.59465 | PASS | 494.6488 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511489 [WTH_JCT4 138.00] TO BUS 511497 [WTH_SE 4 138.00] CKT 1 | 5.4619 | PASS | 0.37861 | PASS | 278.6126 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511489 [WTH_JCT4 138.00] TO BUS 769880 [G22-145-TAP 138.00] CKT 1 | 5.4743 | PASS | 0.37894 | PASS | 278.943 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511490 [ELKCITY6 230.00] TO BUS 511557 [CHISHOLM6 230.00] CKT 1 | 5.7962 | PASS | 0.39118 | PASS | 291.181 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511497 [WTH_SE 4 138.00] TO BUS 511536 [WEATHTP4 138.00] CKT 1 | 5.8945 | PASS | 0.37631 | PASS | 276.3065 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511504 [SAYRE--4 138.00] TO BUS 520903 [ERICK 4 138.00] CKT 1 | 6.6473 | PASS | 0.38932 | PASS | 289.3179 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511506 [WTH WF 4 138.00] TO BUS 511534 [CL-NGTP4 138.00] CKT 1 | 5.8153 | PASS | 0.36824 | PASS | 268.2415 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511506 [WTH WF 4 138.00] TO BUS 511536 [WEATHTP4 138.00] CKT 1 | 5.882 | PASS | 0.37588 | PASS | 275.8819 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511517 [THOMAST2 69.00] TO BUS 511518 [TREFRY 2 69.00] CKT 1 | 6.6542 | PASS | 0.38926 | PASS | 289.2629 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511518 [TREFRY 2 69.00] TO BUS 511519 [T CITY 2 69.00] CKT 1 | 6.6537 | PASS | 0.38926 | PASS | 289.2616 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511522 [FOSSTAP2 69.00] TO BUS 511523 [FOSSPLT2 69.00] CKT 1 | 6.6557 | PASS | 0.38927 | PASS | 289.274 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511532 [WEATHER4 138.00] TO BUS 511536 [WEATHTP4 138.00] CKT 1 | 6.6461 | PASS | 0.38909 | PASS | 289.0939 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511533 [CLIN-NG4 138.00] TO BUS 511534 [CL-NGTP4 138.00] CKT 1 | 6.6286 | PASS | 0.38914 | PASS | 289.136 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511542 [BUFFCK6 230.00] CKT 1 | 6.653 | PASS | 0.38928 | PASS | 289.2796 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511544 [DEMPSEYR_HV 230.00] CKT 1 | 6.6555 | PASS | 0.38928 | PASS | 289.2817 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511547 [ROARK6 230.00] CKT 1 | 6.6527 | PASS | 0.38928 | PASS | 289.2797 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 511557 [CHISHOLM6 230.00] CKT 1 | 6.6156 | PASS | 0.38941 | PASS | 289.4064 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511541 [DEMPSEYR POI 230.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 6.6201 | PASS | 0.38936 | PASS | 289.3629 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 6.6363 | PASS | 0.38928 | PASS | 289.2773 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 6.4868 | PASS | 0.38958 | PASS | 289.5778 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 781591 [GEN-2024-154 345.00] CKT 1 | 6.6615 | PASS | 0.38927 | PASS | 289.2736 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511561 [ELLIS 4 138.00] TO BUS 520459 [CUSTER 4 138.00] CKT 1 | 6.5829 | PASS | 0.38944 | PASS | 289.4415 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511561 [ELLIS 4 138.00] TO BUS 521001 [MORWODS4 138.00] CKT 1 | 6.5875 | PASS | 0.38942 | PASS | 289.4194 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511564 [MARTHA 4 138.00] TO BUS 529302 [OMALTUS4 138.00] CKT 1 | 6.6367 | PASS | 0.38933 | PASS | 289.3296 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 511592 [SEVEN7A_HV 345.00] CKT 1 | 6.6484 | PASS | 0.38928 | PASS | 289.2753 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 6.647 | PASS | 0.38928 | PASS | 289.276 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 6.6258 | PASS | 0.38933 | PASS | 289.3342 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 6.6546 | PASS | 0.38927 | PASS | 289.2726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 2 | 6.6546 | PASS | 0.38927 | PASS | 289.2726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 1 | 6.6365 | PASS | 0.3893 | PASS | 289.2974 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 2 | 6.6365 | PASS | 0.3893 | PASS | 289.2975 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520402 [BULOJ4 138.00] TO BUS 520903 [ERICK 4 138.00] CKT 1 | 6.6473 | PASS | 0.38931 | PASS | 289.3119 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520459 [CUSTER 4 138.00] TO BUS 521116 [REDHLSW4 138.00] CKT 1 | 6.5824 | PASS | 0.38944 | PASS | 289.4442 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520468 [HINTON 4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 6.6553 | PASS | 0.3893 | PASS | 289.2952 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520503 [DEERCR 4 138.00] TO BUS 520950 [HYDRO 4 138.00] CKT 1 | 4.6843 | PASS | 0.40847 | PASS | 308.4745 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520503 [DEERCR 4 138.00] TO BUS 521092 [WEATHFD4 138.00] CKT 1 | 4.685 | PASS | 0.40873 | PASS | 308.7339 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521010 [NIJECT 4 138.00] CKT 1 | 6.6556 | PASS | 0.3893 | PASS | 289.2953 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 4.6952 | PASS | 0.40568 | PASS | 305.6796 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 4.6905 | PASS | 0.40644 | PASS | 306.4377 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520846 [CARTERJ2 69.00] TO BUS 520876 [DILL JT2 69.00] CKT 1 | 6.6336 | PASS | 0.38936 | PASS | 289.3574 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520846 [CARTERJ2 69.00] TO BUS 520978 [LKCREEK2 69.00] CKT 1 | 6.6336 | PASS | 0.38936 | PASS | 289.3575 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520856 [CLINTON4 138.00] TO BUS 521092 [WEATHFD4 138.00] CKT 1 | 4.6824 | PASS | 0.40951 | PASS | 309.5091 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520873 [CANUTE 2 69.00] TO BUS 520875 [DILL 2 69.00] CKT 1 | 6.6555 | PASS | 0.38928 | PASS | 289.2751 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520873 [CANUTE 2 69.00] TO BUS 520876 [DILL JT2 69.00] CKT 1 | 6.6554 | PASS | 0.38928 | PASS | 289.2779 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520876 [DILL JT2 69.00] TO BUS 520897 [ELKCITY2 69.00] CKT 1 | 6.6334 | PASS | 0.38936 | PASS | 289.3648 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520950 [HYDRO 4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 4.6871 | PASS | 0.40754 | PASS | 307.5365 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521001 [MORWODS4 138.00] TO BUS 521002 [MORWOOD4 138.00] CKT 1 | 6.6474 | PASS | 0.3893 | PASS | 289.3049 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521001 [MORWODS4 138.00] TO BUS 521128 [NINMLTP4 138.00] CKT 1 | 6.5221 | PASS | 0.3896 | PASS | 289.6016 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 4.6983 | PASS | 0.40522 | PASS | 305.2172 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521116 [REDHLSW4 138.00] TO BUS 521117 [RHWIND 4 138.00] CKT 1 | 6.6538 | PASS | 0.38947 | PASS | 289.4707 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 6.6327 | PASS | 0.38932 | PASS | 289.3223 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 529298 [OMPVET-4 138.00] TO BUS 529302 [OMALTUS4 138.00] CKT 1 | 6.6372 | PASS | 0.38932 | PASS | 289.3208 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 6.6495 | PASS | 0.3893 | PASS | 289.2982 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511444 [ROSVTAP2 69.00] TO BUS 511432 [R-AMOCO2 69.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2728 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511444 [ROSVTAP2 69.00] TO BUS 511495 [TOMSTEED2 69.00] CKT 1 | 6.6504 | PASS | 0.38928 | PASS | 289.2834 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511459 [ELKCTY-2 69.00] CKT 1 | 6.6326 | PASS | 0.3894 | PASS | 289.4002 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511458 [ELKCTY-4 138.00] TO BUS 511490 [ELKCITY6 230.00] CKT 1 | 5.7962 | PASS | 0.39118 | PASS | 291.181 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511463 [HOB-JCT4 138.00] TO BUS 511464 [HOB-JCT2 69.00] CKT 1 | 6.6499 | PASS | 0.38929 | PASS | 289.2899 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.4.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2737 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.4.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2737 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.00] CKT 1 | 6.6557 | PASS | 0.38928 | PASS | 289.2779 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.8.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 6.6485 | PASS | 0.3893 | PASS | 289.2998 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511484 [CLINTJC2 69.00] TO BUS 511485 [CLINTJC4 138.00] CKT 1 | 6.6147 | PASS | 0.38983 | PASS | 289.8256 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511496 [WTH_SE 2 69.00] TO BUS 511497 [WTH_SE 4 138.00] CKT 1 | 6.6137 | PASS | 0.38909 | PASS | 289.0944 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511506 [WTH WF 4 138.00] TO BUS 511950 [WASHITA 34.5.00] CKT 1 | 6.6691 | PASS | 0.38568 | PASS | 285.6797 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511542 [BUFFCK6 230.00] TO BUS 511959 [BUFFCK1 34.5.00] CKT 1 | 6.6529 | PASS | 0.38928 | PASS | 289.2797 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511544 [DEMPSEYR_HV 230.00] TO BUS 511961 [DEMPSE34.5_1 34.5.00] CKT 1 | 6.6557 | PASS | 0.38928 | PASS | 289.2822 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511547 [ROARK6 230.00] TO BUS 511960 [ROARK1 34.5.00] CKT 1 | 6.6523 | PASS | 0.38928 | PASS | 289.2801 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511557 [CHISHOLM6 230.00] CKT 1 | 6.2627 | PASS | 0.38992 | PASS | 289.9208 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511554 [RKY_RDG4 138.00] TO BUS 511963 [RKYRDGW1-1 34.5.00] CKT 1 | 6.6566 | PASS | 0.38929 | PASS | 289.2872 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511554 [RKY_RDG4 138.00] TO BUS 511962 [RKYRDGW2-1 34.5.00] CKT 1 | 6.6566 | PASS | 0.38929 | PASS | 289.2879 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511563 [ELSWORTH 4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 6.6446 | PASS | 0.38931 | PASS | 289.3118 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 6.646 | PASS | 0.3893 | PASS | 289.3033 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 6.6552 | PASS | 0.38928 | PASS | 289.2797 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511592 [SEVEN7A_HV 345.00] TO BUS 511599 [SEVEN7AB2 345.00] CKT 1 | 6.6512 | PASS | 0.38927 | PASS | 289.2745 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 511592 [SEVEN7A_HV 345.00] TO BUS 511608 [SEVEN7AB3 345.00] CKT 1 | 6.6534 | PASS | 0.38927 | PASS | 289.2733 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 6.6549 | PASS | 0.38927 | PASS | 289.2728 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 6.6549 | PASS | 0.38927 | PASS | 289.2728 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 6.6546 | PASS | 0.38927 | PASS | 289.2738 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 6.6546 | PASS | 0.38927 | PASS | 289.2738 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 6.6544 | PASS | 0.38927 | PASS | 289.2736 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 6.6548 | PASS | 0.38927 | PASS | 289.2726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 6.6548 | PASS | 0.38927 | PASS | 289.2726 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 6.655 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 6.6552 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 6.6548 | PASS | 0.38927 | PASS | 289.273 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 2 | 6.654 | PASS | 0.38927 | PASS | 289.2715 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 3 | 6.6538 | PASS | 0.38927 | PASS | 289.2715 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 525832 [TUCO_INT 7 345.00] CKT 1 | 6.6406 | PASS | 0.3893 | PASS | 289.2976 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 6.6536 | PASS | 0.38928 | PASS | 289.2808 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 6.6155 | PASS | 0.38937 | PASS | 289.3685 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] CKT 3 | 6.5984 | PASS | 0.38946 | PASS | 289.4563 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520402 [BULOJ4 138.00] TO BUS 521060 [SWEETWR4 138.00] CKT 1 | 6.6472 | PASS | 0.38931 | PASS | 289.3129 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.654 | PASS | 0.38929 | PASS | 289.2852 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 2 | 6.6549 | PASS | 0.38928 | PASS | 289.2784 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 3 | 6.6549 | PASS | 0.38928 | PASS | 289.2784 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520422 [SEQUOYAHJ4 138.00] CKT 1 | 6.6538 | PASS | 0.38928 | PASS | 289.2818 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520508 [CLVLDSW4 138.00] CKT 1 | 6.6543 | PASS | 0.38928 | PASS | 289.2766 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.8.00] CKT 1 | 6.6435 | PASS | 0.38929 | PASS | 289.2921 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.8.00] CKT 1 | 6.6435 | PASS | 0.38929 | PASS | 289.292 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.8.00] CKT 1 | 6.6435 | PASS | 0.38929 | PASS | 289.292 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 6.6533 | PASS | 0.38928 | PASS | 289.284 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 6.6539 | PASS | 0.3893 | PASS | 289.2964 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.8.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.8.00] CKT 1 | 6.6499 | PASS | 0.38928 | PASS | 289.2822 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.8.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2724 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.8.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2724 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.8.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 6.6559 | PASS | 0.38927 | PASS | 289.2742 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520810 [ANADARK2 69.00] CKT 1 | 6.6555 | PASS | 0.38927 | PASS | 289.2724 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520978 [LKCREEK2 69.00] TO BUS 520927 [GRANITE2 69.00] CKT 1 | 6.6495 | PASS | 0.38929 | PASS | 289.2938 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520978 [LKCREEK2 69.00] TO BUS 520982 [LONEWLF2 69.00] CKT 1 | 6.6487 | PASS | 0.3893 | PASS | 289.2964 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521000 [MORWODS2 69.00] TO BUS 520457 [BTLRJCT2 69.00] CKT 1 | 6.6549 | PASS | 0.38928 | PASS | 289.279 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521000 [MORWODS2 69.00] TO BUS 521001 [MORWODS4 138.00] CKT 1 | 6.6549 | PASS | 0.38928 | PASS | 289.279 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521002 [MORWOOD4 138.00] TO BUS 520832 [BRANTLEY4 138.00] CKT 1 | 6.6474 | PASS | 0.3893 | PASS | 289.304 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.6274 | PASS | 0.38938 | PASS | 289.3804 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 2 | 6.6347 | PASS | 0.38935 | PASS | 289.3524 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 6.6567 | PASS | 0.38934 | PASS | 289.3427 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 521088 [WASHITA2 69.00] CKT 1 | 6.654 | PASS | 0.38928 | PASS | 289.284 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521117 [RHWIND 4 138.00] TO BUS 521119 [REDHILLS WF1 34.5.00] CKT 1 | 6.6538 | PASS | 0.38947 | PASS | 289.4711 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521128 [NINMLTP4 138.00] TO BUS 520492 [NINMILE4 138.00] CKT 1 | 6.6556 | PASS | 0.38927 | PASS | 289.2724 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521128 [NINMLTP4 138.00] TO BUS 520500 [BEARCAT4 138.00] CKT 1 | 6.5215 | PASS | 0.3896 | PASS | 289.6032 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 6.638 | PASS | 0.3893 | PASS | 289.2992 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523770 [GRAPEVINE 3 115.00] CKT 1 | 6.6552 | PASS | 0.38928 | PASS | 289.2767 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523776 [WHEELER 3 115.00] TO BUS 523772 [COBRN_CREEK3 115.00] CKT 1 | 6.6563 | PASS | 0.38928 | PASS | 289.2751 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523776 [WHEELER 3 115.00] TO BUS 523797 [HOWARD 3 115.00] CKT 1 | 6.6536 | PASS | 0.38928 | PASS | 289.2813 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523776 [WHEELER 3 115.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 6.6545 | PASS | 0.38928 | PASS | 289.2839 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 6.6498 | PASS | 0.38927 | PASS | 289.2709 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 524296 [SPNSPUR_WND7 345.00] CKT 1 | 6.6537 | PASS | 0.38927 | PASS | 289.2722 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 525549 [TOLK 7 345.00] CKT 1 | 6.6537 | PASS | 0.38927 | PASS | 289.2739 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] CKT 1 | 6.6555 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] CKT 1 | 6.6555 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] CKT 1 | 6.6555 | PASS | 0.38927 | PASS | 289.2725 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] CKT 2 | 6.6562 | PASS | 0.38927 | PASS | 289.2741 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] CKT 1 | 6.6552 | PASS | 0.38927 | PASS | 289.2738 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 529298 [OMPVET-4 138.00] TO BUS 529345 [OMPARK-4 138.00] CKT 1 | 6.6374 | PASS | 0.38932 | PASS | 289.3168 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 765890 [GEN-2021-064 138.00] TO BUS 765894 [G21-064-XFM1 34.5.00] CKT 1 | 6.655 | PASS | 0.38927 | PASS | 289.2722 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 769880 [G22-145-TAP 138.00] TO BUS 511433 [HINTON 4 138.00] CKT 1 | 5.3828 | PASS | 0.37906 | PASS | 279.0554 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 769880 [G22-145-TAP 138.00] TO BUS 769881 [GEN-2022-145 138.00] CKT 1 | 6.6815 | PASS | 0.38928 | PASS | 289.2814 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 776561 [GEN-2023-229 138.00] TO BUS 776562 [G23-229XFMR1 34.5.00] CKT 1 | 6.6561 | PASS | 0.38932 | PASS | 289.3218 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 776561 [GEN-2023-229 138.00] TO BUS 776565 [G23-229XFMR2 34.5.00] CKT 1 | 6.656 | PASS | 0.38932 | PASS | 289.3163 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 781591 [GEN-2024-154 345.00] TO BUS 781592 [G24-154XFMR1 34.5.00] CKT 1 | 6.6615 | PASS | 0.38927 | PASS | 289.2736 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 6.6521 | PASS | 0.38927 | PASS | 289.2743 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 6.6504 | PASS | 0.38928 | PASS | 289.2781 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 6.6451 | PASS | 0.38927 | PASS | 289.273 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.6518 | PASS | 0.3893 | PASS | 289.3013 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.6518 | PASS | 0.3893 | PASS | 289.3013 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 2 | 6.6536 | PASS | 0.38929 | PASS | 289.2885 | 31.36 | 36
GEN-2026-PR15 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR15 | 138kV Bus at AEP CLINTON Substation, Custer County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 515802 [GRACMNT4 138.00] CKT 1 | 6.5536 | PASS | 0.38966 | PASS | 289.6637 | 31.36 | 36

## WSCR
* WSCR is not applicable for this study.