## Executive Summary
Executive Summary: Group 05 GEN-2026-PR16 Priority Process Study
Interconnection Customer GEN-2026-PR16 (Group 05) has requested a Priority System Impact Study pursuant to Section 3.11 of the GIP under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR16 generation for total of:
31.82 MW
The minimum cost of interconnecting GEN-2026-PR16 included in this Priority Process is estimated at:
Total Network Upgrade $ 15,270,000 Steady State Network Upgrade $ 15,270,000 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR16 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 8/10/2026
Costs for Wind Requests were allocated using the 29L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4624400% | SPP | Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR16 | 05 SOUTHWEST | 40 | Priority Process | Wind | 31.82 | 0 | 0 | 0 | 0 | 0 | 0 | 31.82 | 31.82 | -0.1 | ER | SPS | Martin 115kV | SPECIAL STUDY
GEN-2026-PR15 | 04 SOUTHEAST | 39 | Priority Process | Wind | 31.36 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | SPECIAL STUDY
GEN-2026-PR14 | 04 SOUTHEAST | 38 | Priority Process | Battery/Storage | 43.99 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | SPECIAL STUDY
GEN-2026-PR13 | 04 SOUTHEAST | 37 | Priority Process | Wind | 25.96 | [9 empty] | ER | OG&E | Minco 345kV Substation | SPECIAL STUDY
GEN-2026-PR12 | 04 SOUTHEAST | 36 | Priority Process | Wind | 11.96 | [9 empty] | ER | OG&E | NARDINS2 69kV | SPECIAL STUDY
GEN-2026-PR11 | 05 SOUTHWEST | 35 | Priority Process | Wind | 30 | [9 empty] | ER | SPS | Lost Draw 3 115kV substation | SPECIAL STUDY
GEN-2026-PR9 | 05 SOUTHWEST | 34 | Priority Process | Wind | 15.99 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | SPECIAL STUDY
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | [9 empty] | ER | MIDW | South Hays 230kV | SPECIAL STUDY
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | SPECIAL STUDY
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | SPECIAL STUDY
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | SPECIAL STUDY
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | SPECIAL STUDY
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR16 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 31.82 | 0 | Non-Convergence | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 31.82 | 31.82
GEN-2026-PR16 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 31.82 | 0 | Non-Convergence | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 31.82 | 31.82
GEN-2026-PR16 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 31.82 | 0 | Non-Convergence | Multiple Upgrades | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 31.82 | N/A
GEN-2026-PR16 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 31.82 | 0 | Non-Convergence | Multiple Upgrades | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 31.82 | N/A
GEN-2026-PR16 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 31.82 | 0 | Non-Convergence | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 31.82 | 31.82
GEN-2026-PR16 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 31.82 | 0 | Non-Convergence | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 31.82 | 31.82
GEN-2026-PR16 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 31.82 | 31.82 | None | 0 | N/A | N/A | N/A | 31.82 | N/A | N/A | N/A | N/A | N/A | 31.82
GEN-2026-PR16 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 31.82 | 31.82 | None | 0 | N/A | N/A | N/A | 31.82 | N/A | N/A | N/A | N/A | N/A | 31.82

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 523928 MARTIN 3 115 523938 PANTEX_N 3 115 1 | 26SP, 29L, 29SP | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | 159 | 175 | 90.81 | 108.53 |  |  |  | Martin to Pantex_N3 115 kV Line Rebuild
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 523931 HIGHLAND_TP3 115 523945 PANTEX_S 3 115 1 | 26SP, 29L | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | 159 | 175 | <90% | 106.11 |  |  |  | Highland to Pantex_N3 115 kV Linex Rebuild
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 523938 PANTEX_N 3 115 523945 PANTEX_S 3 115 1 | 26SP, 29L, 29SP | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | 159 | 175 | <90% | 102.98 |  |  |  | Pantex_N3 to Pantex_S2 115 kV Rebuild
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 26SP | System Intact | 478 | 546 | 118.6 | 118.96 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 26SP | System Intact | 615 | 699 | 126.12 | 126.69 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 26SP | System Intact | 559 | 637 | 120.93 | 121.47 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 26SP | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 1792 | 1792 | 153.12 | 153.5 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 778200 G24-041-TAP 345 1 | 26SP | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 143.27 | 143.7 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 26SP | System Intact | 615 | 699 | 125.52 | 126.07 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 26SP | System Intact | 559 | 637 | 120.36 | 120.88 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 26SP | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 152.99 | 153.43 |  |  |  | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 26SP | System Intact | 478 | 546 | 118.6 | 118.96 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 26SP | System Intact | 615 | 699 | 126.12 | 126.69 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 26SP | System Intact | 559 | 637 | 120.93 | 121.47 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 26SP | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 1792 | 1792 | 153.12 | 153.5 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 778200 G24-041-TAP 345 1 | 26SP | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 143.27 | 143.7 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 26SP | System Intact | 615 | 699 | 125.52 | 126.07 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 26SP | System Intact | 559 | 637 | 120.36 | 120.88 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 26SP | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 152.99 | 153.43 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
05ALL | GEN-2026-PR16 PSIS | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS | ERIS | Thermal | None | 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29L, 29SP | 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29L, 29SP | 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29L, 29SP | 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29L, 29SP | 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | Line - Seminole - Southwest Shreveport 765 kV
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29L, 29SP | 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29L, 29SP | System Intact | [7 empty] | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 29L | System Intact | [7 empty] | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP, 29SP | System Intact | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | Non-Converged | 29L, 29SP | System Intact | [7 empty] | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Non-Converged | None | 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Thermal | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR16 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | 170079, 170091, 170558, 170561 | ERIS | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV | Contingent | Install 765 kV Substation at Phantom and install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation with a summer emergency rating of 5300 MVA. Install three new 765/345 transformers at Phantom 345 kV substation | 0 | 0% | 354167587 | 0.11942
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | 504210 | ERIS | Crawfish Draw - Phantom 765 kV Ckt 1 New Line | Contingent | Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom | 0 | 0% | 896306387.8 | 0.08171
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | TBD | ERIS | Martin to Pantex_N3 115 kV Line Rebuild | Current Study | Rebuild the existing MARTIN 3 to PANTEX_N 3 115 kV line 1 (5.14 miles) to a minimum rating of 239 MVA | 5140000 | 100% | 5140000 | 1
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | TBD | ERIS | Highland to Pantex_N3 115 kV Linex Rebuild | Current Study | Rebuild the existing HIGHLAND_TP3 to PANTEX_S 3 115 kV line 1 (6.78 miles) to a minimum rating of 239 MVA | 6780000 | 100% | 6780000 | 1
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | TBD | ERIS | Pantex_N3 to Pantex_S2 115 kV Rebuild | Current Study | Rebuild the existing PANTEX_N 3 to PANTEX_S 3 115 kV line 1 (3.35 miles) to a minimum rating of 239 MVA | 3350000 | 100% | 3350000 | 1
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | TBD | ERIS | Martin 115kV Substation GEN-2026-PR16 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR16 (31.82/Wind), into Martin 115 kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR16 | GEN-2026-PR16 PSIS | 05 SOUTHWEST | TBD | ERIS | Martin 115kV Substation GEN-2026-PR16 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR16 (31.82/Wind), into Martin 115 kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Contingent | Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola Install new 345/765 kV Ckt 1 transformer at Viola | 0 | 0% | 1149147202 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Contingent | Install new 345/765 kV Ckt 1 transformer at Anthem | 0 | 0% | 61500000 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line | Contingent | Install 345 kV substation at Crawfish Draw | 0 | 0% | 20441838.66 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Contingent | Build a 284.8-mile 765 kV Ckt 1 line from Minco to Crawfish Draw | 0 | 0% | 1646620000 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Line - Seminole - Southwest Shreveport 765 kV | Contingent | Install 157.3 MVAR line reactor at Seminole 765 kV substation toward Southwest Shreveport 765 kV | 0 | 0% | 15730000 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Contingent | Install new 345/765 kV Ckt 1 transformer at Viola | 0 | 0% | 1149147202 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Contingent | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 0 | 0% | 1200600000 | N/A
GEN-2026-PR16 | GEN-2026-PR16 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line | Contingent | Install new 345/765 kV Ckt 1 transformer at Woodward | 0 | 0% | 61500000 | N/A
Total | [7 empty] | 15270000

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV | 170079, 170091, 170558, 170561 | Install 765 kV Substation at Phantom and install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation with a summer emergency rating of 5300 MVA. Install three new 765/345 transformers at Phantom 345 kV substation | SPS | 4798300% | 354167587
Contingent | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line | 504210 | Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom | SPS | 4821400% | 896306387.8
Current Study | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR16 PSIS | ERIS | Martin to Pantex_N3 115 kV Line Rebuild | TBD | Rebuild the existing MARTIN 3 to PANTEX_N 3 115 kV line 1 (5.14 miles) to a minimum rating of 239 MVA | TBD | TBD | 5140000
Current Study | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR16 PSIS | ERIS | Highland to Pantex_N3 115 kV Linex Rebuild | TBD | Rebuild the existing HIGHLAND_TP3 to PANTEX_S 3 115 kV line 1 (6.78 miles) to a minimum rating of 239 MVA | TBD | TBD | 6780000
Current Study | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR16 PSIS | ERIS | Pantex_N3 to Pantex_S2 115 kV Rebuild | TBD | Rebuild the existing PANTEX_N 3 to PANTEX_S 3 115 kV line 1 (3.35 miles) to a minimum rating of 239 MVA | TBD | TBD | 3350000
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | 504296/504304 | Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola Install new 345/765 kV Ckt 1 transformer at Viola | TBD/WERE | 4821400% | 1149147202
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | 504184 | Install new 345/765 kV Ckt 1 transformer at Anthem | AEP | 4821400% | 61500000
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line | 504216 | Install 345 kV substation at Crawfish Draw | TBD | 4821400% | 20441838.66
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | 504172 | Build a 284.8-mile 765 kV Ckt 1 line from Minco to Crawfish Draw | TBD | 4821400% | 1646620000
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Seminole - Southwest Shreveport 765 kV | 504252 | Install 157.3 MVAR line reactor at Seminole 765 kV substation toward Southwest Shreveport 765 kV | SPS | 4821400% | 15730000
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | 504304 | Install new 345/765 kV Ckt 1 transformer at Viola | WERE | 4821400% | 1149147202
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | 504237 | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | TBD | 4821400% | 1200600000
Contingent | GEN-2026-PR16 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line | 504285 | Install new 345/765 kV Ckt 1 transformer at Woodward | OGE | 4821400% | 61500000
Interconnection | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR16 PSIS | ERIS | Martin 115kV Substation GEN-2026-PR16 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR16 (31.82/Wind), into Martin 115 kV Substation | SPS | TBD | TBD
Interconnection | GEN-2026-PR16 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR16 PSIS | ERIS | Martin 115kV Substation GEN-2026-PR16 Interconnection (Non-Shared NU) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR16 (31.82/Wind), into Martin 115 kV Substation | SPS | TBD | TBD
6570430217.46

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 500753 | Carpenter 345 kV New Capacitor | Carpenter 345 kV Capacitor | Install 90 MVAR capacitor at Carpenter 345 kV substation | 2025 ITP | Yes | N/A | 0.07819 | 4821400% | 5121041.84
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502639 | Potter Co - Harrington 230 kV New Line | Potter Co - Harrington 230 kV Ckt 2 New Line | Build a 11.93-mile 230 kV Ckt 2 line from Potter Co to Harrington | 2025 ITP | Yes | N/A | 0.19273 | 4821400% | 28432656.725
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502642 | Potter Co - Harrington 230 kV New Line | Potter Co 230 kV Ckt 2 Terminal Upgrade toward Harrington 230 kV | Upgrade terminal equipment at Potter Co 230 kV substation for Ckt 2 toward Harrington 230 kV | 2025 ITP | Yes | N/A | 0.19273 | 4821400% | 3600000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502643 | Potter Co - Harrington 230 kV New Line | Harrington 230 kV Ckt 2 Terminal Upgrade toward Potter Co 230 kV | Upgrade terminal equipment at Harrington 230 kV substation for Ckt 2 toward Potter Co 230 kV | 2025 ITP | Yes | N/A | 0.19273 | 4821400% | 3600000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502644 | Harrington - Rolling Hills 230 kV New Line | Harrington - Rolling Hills 230 kV Ckt 2 New Line | Build a 6.36-mile 230 kV Ckt 2 line from Harrington to Rolling Hills | 2025 ITP | Yes | N/A | 0.07512 | 4821400% | 15157728.1451
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502647 | Harrington - Rolling Hills 230 kV New Line | Harrington 230 kV Ckt 2 Terminal Upgrade toward Rolling Hills 230 kV | Upgrade terminal equipment at Harrington 230 kV substation for Ckt 2 toward Rolling Hills 230 kV | 2025 ITP | Yes | N/A | 0.07512 | 4821400% | 3600000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502648 | Harrington - Rolling Hills 230 kV New Line | Rolling Hills 230 kV Ckt 2 Terminal Upgrade toward Harrington 230 kV | Upgrade terminal equipment at Rolling Hills 230 kV substation for Ckt 2 toward Harrington 230 kV | 2025 ITP | Yes | N/A | 0.07512 | 4821400% | 3600000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 500466 | Line - Crawfish Draw - Phantom 765 kV New Line | Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw | Tap the existing Border - Tuco 345 kV Ckt 1 line and extend 4.8 miles to new Crawfish Draw substation | 2025 ITP | Yes | N/A | 0.04144 | 4821400% | 3100000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504210 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw - Phantom 765 kV Ckt 1 New Line | Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 896306387.8
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504212 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV Ckt 1 Terminal Upgrade toward Phantom 765 kV | Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 1 toward Phantom 765 kV | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 1567814
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504213 | Line - Crawfish Draw - Phantom 765 kV New Line | Phantom 765 kV Ckt 1 Terminal Upgrade toward Crawfish Draw 765 kV | Upgrade terminal equipment at Phantom 765 kV substation for Ckt 1 toward Crawfish Draw 765 kV | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 11724000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504214 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV Line Reactor | Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation toward Phantom 765 kV | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 12271304.934
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504215 | Line - Crawfish Draw - Phantom 765 kV New Line | Phantom 765 kV Line Reactor | Install 119.6 MVAR line reactor at Phantom 765 kV substation toward Crawfish Draw 765 kV | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 34195000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504216 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 345 kV New Substation | Install 345 kV substation at Crawfish Draw | 2025 ITP | Yes | N/A | 0.04144 | 4821400% | 20441838.66
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504179 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV New Substation | Install 765 kV substation at Crawfish Draw | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 47284600.47
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504217 | Line - Crawfish Draw - Phantom 765 kV New Line | Oklaunion 345 kV Reactor | Install 75 MVAR reactor at Oklaunion 345 kV substation | 2025 ITP | Yes | N/A | 0.03103 | 4821400% | 7500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504221 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 345 kV Reactor | Install 175 MVAR reactor at Crawfish Draw 345 kV substation | 2025 ITP | Yes | N/A | 0.04144 | 4821400% | 16256703.7325
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504223 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV Reactor | Install 375 MVAR reactor at Crawfish Draw 765 kV substation | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 12271304.934
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504225 | Line - Crawfish Draw - Phantom 765 kV New Line | Phantom 765 kV Reactor | Install 300 MVAR reactor at Phantom 765 kV substation | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 34195000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502134 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Crawfish Draw - Phantom 765 kV Ckt 2 New Line | Build a 238.6-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 896306387.8
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502135 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Crawfish Draw 765 kV Ckt 2 Terminal Upgrade toward Phantom 765 kV | Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 2 toward Phantom 765 kV | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 1567814
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 502136 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Phantom 765 kV Ckt 2 Terminal Upgrade toward Crawfish Draw 765 kV | Upgrade terminal equipment at Phantom 765 kV substation for Ckt 2 toward Crawfish Draw 765 kV | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 11724000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504235 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Crawfish Draw 765 kV Line Reactor | Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 12271304.934
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504236 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Phantom 765 kV Line Reactor | Install 119.6 MVAR line reactor at Phantom 765 kV substation | 2025 ITP | Yes | N/A | 0.06482 | 4821400% | 34195000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504237 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward - Potter Co 765 kV Ckt 1 New Line | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 2025 ITP | Yes | N/A | 0.26884 | 4821400% | 1200600000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504239 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward 765 kV Ckt 1 Terminal Upgrade toward Potter Co 765 kV | Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Potter Co 765 kV | 2025 ITP | Yes | N/A | 0.26884 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504240 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Potter Co 765 kV Ckt 1 Terminal Upgrade toward Woodward 765 kV | Upgrade terminal equipment at Potter Co 765 kV substation for Ckt 1 toward Woodward 765 kV | 2025 ITP | Yes | N/A | 0.26884 | 4821400% | 11724000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504241 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward 765 kV Line Reactor | Install 104 MVAR line reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 30000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504242 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Potter Co 765 kV Line Reactor | Install 104 MVAR line reactor at Potter Co 765 kV substation | 2025 ITP | Yes | N/A | 0.26884 | 4821400% | 10400000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504243 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 30000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504245 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 13000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504247 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Potter Co 765 kV Reactor | Install 225 MVAR reactor at Potter Co 765 kV substation | 2025 ITP | Yes | N/A | 0.26884 | 4821400% | 22500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504248 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.6-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | 0.03974 | 4821400% | 1822360000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504249 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Ckt 1 Terminal Upgrade toward Seminole 765 kV | Upgrade terminal equipment at Southwest Shreveport 765 kV substation for Ckt 1 toward Seminole 765 kV | 2025 ITP | Yes | N/A | 0.03974 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504250 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Ckt 1 Terminal Upgrade toward Southwest Shreveport 765 kV | Upgrade terminal equipment at Seminole 765 kV substation for Ckt 1 toward Southwest Shreveport 765 kV | 2025 ITP | Yes | N/A | 0.03974 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504251 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Line Reactor | Install 157.3 MVAR line reactor at Southwest Shreveport 765 kV substation toward Seminole 765 kV | 2025 ITP | Yes | N/A | 0.03974 | 4821400% | 15730000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504252 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Line Reactor | Install 157.3 MVAR line reactor at Seminole 765 kV substation toward Southwest Shreveport 765 kV | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 15730000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504253 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV New Substation | Install 765 kV substation at Southwest Shreveport | 2025 ITP | Yes | N/A | 0.03974 | 4821400% | 27000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504254 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV New Substation | Install 765 kV substation at Seminole | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 27000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504255 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Reactor | Install 150 MVAR reactor at Southwest Shreveport 765 kV substation | 2025 ITP | Yes | N/A | 0.03974 | 4821400% | 15000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504257 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Reactor | Install 150 MVAR reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 15000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504282 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Line Reactor | Install 131.95 MVAR line reactor at Woodward 765 kV substation toward Crawfish Draw 765 kV | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 30000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504283 | Line - Woodward - Crawfish Draw 765 kV New Line | Crawfish Draw 765 kV Line Reactor | Install 131.95 MVAR line reactor at Crawfish Draw 765 kV substation toward Woodward 765 kV | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 12271304.934
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504284 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV New Substation | Install 765 kV substation at Woodward | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 27000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504245 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 13000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504243 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 30000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504285 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Woodward | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 61500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504286 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345 kV Ckt 1 Terminal Upgrade toward Woodward 765 kV | Upgrade terminal equipment at Woodward 345 kV substation for Ckt 1 toward Woodward 765 kV | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504287 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Ckt 1 Terminal Upgrade toward Woodward 345 kV | Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Woodward 345 kV | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504288 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Woodward | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 61500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504289 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345 kV Ckt 2 Terminal Upgrade toward Woodward 765 kV | Upgrade terminal equipment at Woodward 345 kV substation for Ckt 2 toward Woodward 765 kV | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504290 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Ckt 2 Terminal Upgrade toward Woodward 345 kV | Upgrade terminal equipment at Woodward 765 kV substation for Ckt 2 toward Woodward 345 kV | 2025 ITP | Yes | N/A | 0.03683 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504294 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward 765 kV Line Reactor | Install 70.4 MVAR line reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 30000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504166 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Seminole 765 kV Line Reactor | Install 65.65 MVAR line reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 6565000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504167 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Seminole 765 kV Ckt 1 New Line | Build a 99.8-mile 765 kV Ckt 1 line from Minco to Seminole | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 580000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504168 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Ckt 1 Terminal Upgrade toward Seminole 765 kV | Upgrade terminal equipment at Minco 765 kV substation for Ckt 1 toward Seminole 765 kV | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504169 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Seminole 765 kV Ckt 1 Terminal Upgrade toward Minco 765 kV | Upgrade terminal equipment at Seminole 765 kV substation for Ckt 1 toward Minco 765 kV | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504170 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Line Reactor | Install 49.9 MVAR line reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 4990000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504171 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Seminole 765 kV Line Reactor | Install 49.9 MVAR line reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 4990000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504172 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Crawfish Draw 765 kV Ckt 1 New Line | Build a 284.8-mile 765 kV Ckt 1 line from Minco to Crawfish Draw | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 1646620000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504173 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Ckt 1 Terminal Upgrade toward Crawfish Draw 765 kV | Upgrade terminal equipment at Minco 765 kV substation for Ckt 1 toward Crawfish Draw 765 kV | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504174 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Crawfish Draw 765 kV Ckt 1 Terminal Upgrade toward Minco 765 kV | Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 1 toward Minco 765 kV | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 1567814
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504170 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Line Reactor | Install 49.9 MVAR line reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 4990000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504176 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Crawfish Draw 765 kV Line Reactor | Install 142.4 MVAR line reactor at Crawfish Draw 765 kV substation | 2025 ITP | Yes | N/A | 0.14789 | 4821400% | 12271304.934
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504178 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV New Substation | Install 765 kV substation at Minco | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 27000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504182 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Reactor | Install 150 MVAR reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | 0.10364 | 4821400% | 15000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 883920000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504292 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward 765 kV Ckt 1 Terminal Upgrade toward Viola 765 kV | Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Viola 765 kV | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504293 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Ckt 1 Terminal Upgrade toward Woodward 765 kV | Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Woodward 765 kV | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 27499889
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504296 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | 0.07424 | 4821400% | 1044580000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504297 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem 765 kV Ckt 1 Terminal Upgrade toward Viola 765 kV | Upgrade terminal equipment at Anthem 765 kV substation for Ckt 1 toward Viola 765 kV | 2025 ITP | Yes | N/A | 0.07424 | 4821400% | 18000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504298 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Ckt 1 Terminal Upgrade toward Anthem 765 kV | Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Anthem 765 kV | 2025 ITP | Yes | N/A | 0.07424 | 4821400% | 27499889
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504301 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV New Substation | Install 765 kV substation at Viola | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 107081651
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504180 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem 765 kV Reactor | Install 150 MVAR reactor at Anthem 765 kV substation | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 15000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504302 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Reactor | Install 150 MVAR reactor at Viola 765 kV substation | 2025 ITP | Yes | N/A | 0.22377 | 4821400% | 266653225
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504304 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Viola | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 104567202
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504306 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345 kV Ckt 1 Terminal Upgrade toward Viola 765 kV | Upgrade terminal equipment at Viola 345 kV substation for Ckt 1 toward Viola 765 kV | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504307 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Ckt 1 Terminal Upgrade toward Viola 345 kV | Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Viola 345 kV | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504308 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Viola | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 104567202
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504309 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345 kV Ckt 2 Terminal Upgrade toward Viola 765 kV | Upgrade terminal equipment at Viola 345 kV substation for Ckt 2 toward Viola 765 kV | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504310 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Ckt 2 Terminal Upgrade toward Viola 345 kV | Upgrade terminal equipment at Viola 765 kV substation for Ckt 2 toward Viola 345 kV | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504311 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Viola | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 104567202
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504312 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345 kV Ckt 3 Terminal Upgrade toward Viola 765 kV | Upgrade terminal equipment at Viola 345 kV substation for Ckt 3 toward Viola 765 kV | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504313 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Ckt 3 Terminal Upgrade toward Viola 345 kV | Upgrade terminal equipment at Viola 765 kV substation for Ckt 3 toward Viola 345 kV | 2025 ITP | Yes | N/A | 0.04984 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504177 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 765 kV New Substation | Install 765 kV substation at Anthem | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 249442526.4015
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504180 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 765 kV Reactor | Install 150 MVAR reactor at Anthem 765 kV substation | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 15000000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504184 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 61500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504186 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345 kV Ckt 1 Terminal Upgrade toward Anthem 765 kV | Upgrade terminal equipment at Anthem 345 kV substation for Ckt 1 toward Anthem 765 kV | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504187 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 765 kV Ckt 1 Terminal Upgrade toward Anthem 345 kV | Upgrade terminal equipment at Anthem 765 kV substation for Ckt 1 toward Anthem 345 kV | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504188 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 61500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504189 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345 kV Ckt 2 Terminal Upgrade toward Anthem 765 kV | Upgrade terminal equipment at Anthem 345 kV substation for Ckt 2 toward Anthem 765 kV | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504190 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 765 kV Ckt 2 Terminal Upgrade toward Anthem 345 kV | Upgrade terminal equipment at Anthem 765 kV substation for Ckt 2 toward Anthem 345 kV | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504191 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 61500000
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504192 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345 kV Ckt 3 Terminal Upgrade toward Anthem 765 kV | Upgrade terminal equipment at Anthem 345 kV substation for Ckt 3 toward Anthem 765 kV | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 1537869
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 504193 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 765 kV Ckt 3 Terminal Upgrade toward Anthem 345 kV | Upgrade terminal equipment at Anthem 765 kV substation for Ckt 3 toward Anthem 345 kV | 2025 ITP | Yes | N/A | 0.03102 | 4821400% | 1615723.6181
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 122848 | Minco 345 kV Terminal Equipment | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | N/A | 0.03761 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 133085 | Minco - Pleasant Valley 345 kV Ckt 1 | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | N/A | 0.03761 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 158632 | Potter County 345 kV Substation Expansion | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | N/A | 0.17925 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 158452 | Benton 345 kV Terminal Upgrade | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | N/A | 0.03464 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 158453 | Wichita 345 kV Terminal Upgrade | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | N/A | 0.03464 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | N/A | 0.0581 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | N/A | 0.04082 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | DISIS-2018-001 | Yes | N/A | 0.03946 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build a Second 345-115kV Transformer at Red Willow | Build a Second 345-115kV Transformer at Red Willow | Build a second 345/115kV transformer at Red Willow | DISIS-2018-001 | Yes | N/A | 0.03946 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | N/A | 0.08315 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Sweetwater to Demarcation 230 kV Line Rebuild | Sweetwater to Demarcation 230 kV Line Rebuild | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | DISIS-2018-002/2019-001 | Yes | N/A | 0.08839 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | DISIS-2020-001 | Yes | N/A | 0.04144 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | N/A | 0.03946 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | N/A | 0.03867 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | N/A | 0.04262 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | N/A | 0.04262 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | N/A | 0.0581 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | N/A | 0.07819 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | N/A | 0.07819 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | N/A | 0.04297 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | N/A | 0.07819 | TBD | TBD
GEN-2026-PR16 | 05 SOUTHWEST | ER | TBD |  | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | N/A | 0.03946 | TBD | TBD

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR16 | 05 SOUTHWEST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.0029 | -0.092278 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00538 | -0.17119 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00131 | -0.041684 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00131 | -0.041684 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.00027 | 0.0085914 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00841 | 0.26761 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.00246 | 0.078277 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 2e-05 | 0.0006364 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 2e-05 | 0.0006364 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00056 | 0.017819 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00054 | 0.017183 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00269 | 0.085596 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00051 | 0.016228 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.0006 | -0.019092 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.0006 | -0.019092 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00877 | -0.27906 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.00595 | -0.18933 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | -7e-05 | -0.0022274 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 7e-05 | 0.0022274 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00016 | 0.0050912 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00017 | 0.0054094 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00028 | 0.0089096 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00029 | 0.0092278 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.0003182 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.0003182 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.0003182 | FALSE
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.0003182 | FALSE

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR16 | 05 SOUTHWEST | G05 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.05126 | 118.96 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.11212 | 126.69 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.09771 | 121.47 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 0.24769 | 153.5 | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 0.24769 | 143.94 | 525832 TUCO_INT 7 345 778200 G24-041-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525832 TUCO_INT 7 345 778200 G24-041-TAP 345 1 | 1792 | 1792 | 0.24769 | 143.7 | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.11212 | 126.07 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.09771 | 120.88 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 1792 | 1792 | 0.24769 | 153.43 | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.05126 | 118.96 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.11212 | 126.69 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.09771 | 121.47 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 0.24769 | 153.5 | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 1792 | 1792 | 0.24769 | 143.94 | 525832 TUCO_INT 7 345 778200 G24-041-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | FROM->TO | 525832 TUCO_INT 7 345 778200 G24-041-TAP 345 1 | 1792 | 1792 | 0.24769 | 143.7 | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.11212 | 126.07 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.09771 | 120.88 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 1792 | 1792 | 0.24769 | 153.43 | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 29L | GEN-2026-PR16 | TO->FROM | 523928 MARTIN 3 115 523938 PANTEX_N 3 115 1 | 159 | 175 | 1 | 108.53 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Martin to Pantex_N3 115 kV Line Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 523928 MARTIN 3 115 523938 PANTEX_N 3 115 1 | 159 | 175 | 1 | 107.1 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Martin to Pantex_N3 115 kV Line Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 29SP | GEN-2026-PR16 | TO->FROM | 523928 MARTIN 3 115 523938 PANTEX_N 3 115 1 | 159 | 175 | 1 | 106.76 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Martin to Pantex_N3 115 kV Line Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 523931 HIGHLAND_TP3 115 523945 PANTEX_S 3 115 1 | 159 | 175 | 1 | 100.81 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Highland to Pantex_N3 115 kV Linex Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 29L | GEN-2026-PR16 | TO->FROM | 523931 HIGHLAND_TP3 115 523945 PANTEX_S 3 115 1 | 159 | 175 | 1 | 106.11 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Highland to Pantex_N3 115 kV Linex Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR16 | TO->FROM | 523938 PANTEX_N 3 115 523945 PANTEX_S 3 115 1 | 159 | 175 | 1 | 102.98 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Pantex_N3 to Pantex_S2 115 kV Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 29L | GEN-2026-PR16 | TO->FROM | 523938 PANTEX_N 3 115 523945 PANTEX_S 3 115 1 | 159 | 175 | 1 | 102.25 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Pantex_N3 to Pantex_S2 115 kV Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 29SP | GEN-2026-PR16 | TO->FROM | 523938 PANTEX_N 3 115 523945 PANTEX_S 3 115 1 | 159 | 175 | 1 | 100.45 | P12:115:SPS:T93.1.HUTCH.MARTIN:::HV: | TDF Impact | Pantex_N3 to Pantex_S2 115 kV Rebuild
Thermal | GEN-2026-PR16 PSIS | 05ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR16 PSIS | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR16 PSIS | 05ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR16 PSIS | 05ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR16 PSIS | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR16 PSIS CF | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR16 PSIS CF | 05ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR16 PSIS CF | 05ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR16 PSIS CF | 05ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.20517 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.20517 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.20517 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.20517 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Seminole - Southwest Shreveport 765 kV
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.20517 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.20517 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0 | 0 | 509916 ANTHEM9 765 509915 ANTHEM7 345 1 | TDF Impact | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.29609 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.29609 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.29609 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Seminole - Southwest Shreveport 765 kV
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.29609 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.29609 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.338 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.338 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.338 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.338 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Line - Seminole - Southwest Shreveport 765 kV
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0.338 | 0 | 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | 0 | 0 | 532828 VIOLA9 765 532798 VIOLA 7 345 1 | TDF Impact | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 26SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29L | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Non-Converged | GEN-2026-PR16 PSIS CF | 05ALL | 0 | 29SP | GEN-2026-PR16 | 0 | Non-Converged | 0 | 0 | N/A | 0 | System Intact | TDF Impact | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR16 PSIS | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS | 05ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS CF | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS CF | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS CF | 05ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR16 PSIS CF | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE_TR 1 (523265) 13.2 kV to PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EPLANT_TR3 1 (524160) 13.2 kV to EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LANOGSU (523812). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on YARNELL_TP 3115.00 (524072) 115 kV Bus a. Apply fault at the YARNELL_TP 3115.00 (524072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.2. YARNELL_TP 3 (524072) 115.0 kV to CONWAY 3 (524079) 115.0 kV Transmission Circuit #1 b.3. CONWAY 3 (524079) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on RB-SNEED +3115.00 (523367) 115 kV Bus a. Apply fault at the RB-SNEED +3115.00 (523367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. RB-SNEED 3 (523366) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to HERRING 3 (523359) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.5. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.4. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on WHITAKER 3115.00 (524058) 115 kV Bus a. Apply fault at the WHITAKER 3115.00 (524058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. WHITAKER 3 (524058) 115.0 kV to CENTERPORT 3 (524138) 115.0 kV Transmission Circuit #1 b.3. CENTERPORT 3 (524138) 115.0 kV to EAST_PLANT 3 (524162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on CRMWA_#1TP 3115.00 (523404) 115 kV Bus a. Apply fault at the CRMWA_#1TP 3115.00 (523404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on ASARCO 3115.00 (524016) 115 kV Bus a. Apply fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on MARTIN 3115.00 (523928) 115 kV Bus a. Apply fault at the MARTIN 3115.00 (523928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on ROLLHILLS 3115.00 (524007) 115 kV Bus a. Apply fault at the ROLLHILLS 3115.00 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on Q_RYTON_TP 3115.00 (523478) 115 kV Bus a. Apply fault at the Q_RYTON_TP 3115.00 (523478) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on HERRING_TP 3115.00 (523352) 115 kV Bus a. Apply fault at the HERRING_TP 3115.00 (523352) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to ROCKYPOINT 2 (523397) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on CRMWA_#4 3115.00 (523410) 115 kV Bus a. Apply fault at the CRMWA_#4 3115.00 (523410) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on CAMX/AGR TP3115.00 (523485) 115 kV Bus a. Apply fault at the CAMX/AGR TP3115.00 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SPRINGCREEK269.000 (523512) 69 kV Bus a. Apply fault at the SPRINGCREEK269.000 (523512) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGCREEK2 (523512) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on BURNETT 269.000 (523602) 69 kV Bus a. Apply fault at the BURNETT 269.000 (523602) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURNETT 2 (523602) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on ROXANA 269.000 (523609) 69 kV Bus a. Apply fault at the ROXANA 269.000 (523609) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROXANA 2 (523609) 69.0 kV to DAMRON 2 (523616) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on DAMRON 269.000 (523616) 69 kV Bus a. Apply fault at the DAMRON 269.000 (523616) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on CRMWA#21 269.000 (523646) 69 kV Bus a. Apply fault at the CRMWA#21 269.000 (523646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#21 2 (523646) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on CRMWA#23TP 269.000 (523647) 69 kV Bus a. Apply fault at the CRMWA#23TP 269.000 (523647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#23TP 2 (523647) 69.0 kV to CRMWA#23 2 (523649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on MCCULUGH_TP269.000 (523700) 69 kV Bus a. Apply fault at the MCCULUGH_TP269.000 (523700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCULUGH_TP2 (523700) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on MIDSTRM_TP 3115.00 (523817) 115 kV Bus a. Apply fault at the MIDSTRM_TP 3115.00 (523817) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on ASARCO_TP 3115.00 (524018) 115 kV Bus a. Apply fault at the ASARCO_TP 3115.00 (524018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR11 (523710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR21 (523709) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV to GRAPEVN_TR11 (523769) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR1 1 (524361) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR2 1 (524360) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on MAJESTC_WND3115.00 (523926) 115 kV Bus a. Apply fault at the MAJESTC_WND3115.00 (523926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAJESTC_WND3 (523926) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL (523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 b.5. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply Fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 b.6. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. PRINGLE 1 (523261) 34.5 kV to PRINGLE 3 (523266) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.3. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RVRVIEW_TR11 (523375) 13.2 kV to RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV Three Winding #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 b.2. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on PANTEX_S 3115.00 (523945) 115 kV Bus a. Apply Fault at the PANTEX_S 3115.00 (523945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.2. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.3. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.4. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 b.5. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.6. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.7. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.8. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.9. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.10. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.11. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.12. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.13. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.14. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.9. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.4. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.5. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.6. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.7. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.8. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.9. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.10. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.7. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.8. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.10. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.11. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.13. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.14. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.3. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.4. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.7. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.8. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.10. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.11. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.12. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.13. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.15. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.16. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CARSON_SUB 3115.00 (523924) 115 kV Bus a. Apply Fault at the CARSON_SUB 3115.00 (523924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARSON_SUB 3 (523924) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.3. HPW_COL 1 (523920) 13.2 kV to CARSON_SUB 1 (523923) 13.2 kV Transmission Circuit #1 b.4. CARSON_SUB 1 (523923) 13.2 kV to CARSON_SUB 3 (523924) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.8. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.9. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.10. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ASARCO 3115.00 (524016) 115 kV Bus a. Apply Fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. ASARCO 3 (524016) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.6. BLACKHAWK1 1 (523461) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.5. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.6. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. BLACKHAWK2 1 (523462) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.4. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 b.5. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 b.6. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 b.7. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.3. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.2. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.3. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.4. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR21 (524042) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #2 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.5. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.8. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.9. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.3. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.9. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.10. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.11. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.12. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.6. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 b.2. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.9. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.10. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.11. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.12. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.13. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.14. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.15. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.16. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.17. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.18. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.19. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.20. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 b.7. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply Fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to RIVERVIEW 2 (523376) 69.0 kV Transmission Circuit #1 b.2. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply Fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 b.2. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply Fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to BLACKHAWK 2 (523445) 69.0 kV Transmission Circuit #1 b.2. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply Fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHERLY 2 (523526) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.2. HUTCHISON 2 (523543) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HERRING_TP 3 (523352) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to HARRNG_WST 6 (523977) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to GRAY_CNTY 3 (523636) 115.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply Fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to CAMX/AGR TP3 (523485) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to BLKHAWK_W 3 (523344) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PANTEX_N 3 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on HUTCHISON 2 (523543) 69 kV Bus a. Apply Fault at the HUTCHISON 2 (523543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.2. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Voltage protection trips A23-001-GEN (775724). Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Woodward - Potter Co 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.8. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.9. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.10. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G24-041-TAP 345.00 (778200) 345 kV Bus a. Apply Fault at the G24-041-TAP 345.00 (778200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-041-TAP (778200) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G24-041-TAP (778200) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Voltage protection trips A23-001-GEN (775724). Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Woodward - Potter Co 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LANOGSU (523812). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.2. NICHOLS_3 1 (524023) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Voltage protection trips A23-001-GEN (775724). Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Woodward - Potter Co 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_021 | Single Phase Fault with Stuck Breaker on HARRINGTON-G1 (523977) 230 kV Bus a. Apply Fault at the HARRINGTON-G1 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to remove bus # b.5. HARRNGTON1 1 (523971) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_022 | Single Phase Fault with Stuck Breaker on HARRINGTON-G2 (523978) 230 kV Bus a. Apply Fault at the HARRINGTON-G2 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to remove bus # b.4. HARRNGTON2 1 (523972) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE_TR 1 (523265) 13.2 kV to PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EPLANT_TR3 1 (524160) 13.2 kV to EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on YARNELL_TP 3115.00 (524072) 115 kV Bus a. Apply fault at the YARNELL_TP 3115.00 (524072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.2. YARNELL_TP 3 (524072) 115.0 kV to CONWAY 3 (524079) 115.0 kV Transmission Circuit #1 b.3. CONWAY 3 (524079) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on RB-SNEED +3115.00 (523367) 115 kV Bus a. Apply fault at the RB-SNEED +3115.00 (523367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. RB-SNEED 3 (523366) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to HERRING 3 (523359) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.5. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.4. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on WHITAKER 3115.00 (524058) 115 kV Bus a. Apply fault at the WHITAKER 3115.00 (524058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. WHITAKER 3 (524058) 115.0 kV to CENTERPORT 3 (524138) 115.0 kV Transmission Circuit #1 b.3. CENTERPORT 3 (524138) 115.0 kV to EAST_PLANT 3 (524162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on CRMWA_#1TP 3115.00 (523404) 115 kV Bus a. Apply fault at the CRMWA_#1TP 3115.00 (523404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on ASARCO 3115.00 (524016) 115 kV Bus a. Apply fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on MARTIN 3115.00 (523928) 115 kV Bus a. Apply fault at the MARTIN 3115.00 (523928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on ROLLHILLS 3115.00 (524007) 115 kV Bus a. Apply fault at the ROLLHILLS 3115.00 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on Q_RYTON_TP 3115.00 (523478) 115 kV Bus a. Apply fault at the Q_RYTON_TP 3115.00 (523478) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on HERRING_TP 3115.00 (523352) 115 kV Bus a. Apply fault at the HERRING_TP 3115.00 (523352) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to ROCKYPOINT 2 (523397) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on CRMWA_#4 3115.00 (523410) 115 kV Bus a. Apply fault at the CRMWA_#4 3115.00 (523410) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on CAMX/AGR TP3115.00 (523485) 115 kV Bus a. Apply fault at the CAMX/AGR TP3115.00 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SPRINGCREEK269.000 (523512) 69 kV Bus a. Apply fault at the SPRINGCREEK269.000 (523512) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGCREEK2 (523512) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on BURNETT 269.000 (523602) 69 kV Bus a. Apply fault at the BURNETT 269.000 (523602) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURNETT 2 (523602) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on ROXANA 269.000 (523609) 69 kV Bus a. Apply fault at the ROXANA 269.000 (523609) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROXANA 2 (523609) 69.0 kV to DAMRON 2 (523616) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on DAMRON 269.000 (523616) 69 kV Bus a. Apply fault at the DAMRON 269.000 (523616) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on CRMWA#21 269.000 (523646) 69 kV Bus a. Apply fault at the CRMWA#21 269.000 (523646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#21 2 (523646) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on CRMWA#23TP 269.000 (523647) 69 kV Bus a. Apply fault at the CRMWA#23TP 269.000 (523647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#23TP 2 (523647) 69.0 kV to CRMWA#23 2 (523649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on MCCULUGH_TP269.000 (523700) 69 kV Bus a. Apply fault at the MCCULUGH_TP269.000 (523700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCULUGH_TP2 (523700) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on MIDSTRM_TP 3115.00 (523817) 115 kV Bus a. Apply fault at the MIDSTRM_TP 3115.00 (523817) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on ASARCO_TP 3115.00 (524018) 115 kV Bus a. Apply fault at the ASARCO_TP 3115.00 (524018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR11 (523710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR21 (523709) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV to GRAPEVN_TR11 (523769) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR1 1 (524361) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR2 1 (524360) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on MAJESTC_WND3115.00 (523926) 115 kV Bus a. Apply fault at the MAJESTC_WND3115.00 (523926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAJESTC_WND3 (523926) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-015-GEN (762463 and 762466). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 b.5. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply Fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 b.6. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. PRINGLE 1 (523261) 34.5 kV to PRINGLE 3 (523266) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.3. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RVRVIEW_TR11 (523375) 13.2 kV to RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV Three Winding #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 b.2. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on PANTEX_S 3115.00 (523945) 115 kV Bus a. Apply Fault at the PANTEX_S 3115.00 (523945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.2. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.3. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.4. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 b.5. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.6. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.7. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.8. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.9. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.10. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.11. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.12. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.13. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.14. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.9. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.4. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.5. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.6. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.7. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.8. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.9. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.10. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.7. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.8. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.10. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.11. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.13. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.14. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.3. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.4. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.7. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.8. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.10. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.11. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.12. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.13. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.15. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.16. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CARSON_SUB 3115.00 (523924) 115 kV Bus a. Apply Fault at the CARSON_SUB 3115.00 (523924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARSON_SUB 3 (523924) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.3. HPW_COL 1 (523920) 13.2 kV to CARSON_SUB 1 (523923) 13.2 kV Transmission Circuit #1 b.4. CARSON_SUB 1 (523923) 13.2 kV to CARSON_SUB 3 (523924) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.8. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.9. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.10. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ASARCO 3115.00 (524016) 115 kV Bus a. Apply Fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. ASARCO 3 (524016) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.6. BLACKHAWK1 1 (523461) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.5. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.6. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. BLACKHAWK2 1 (523462) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.4. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 b.5. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 b.6. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 b.7. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.3. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.2. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.3. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.4. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR21 (524042) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #2 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.5. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.8. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.9. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.3. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.9. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.10. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.11. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.12. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.6. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 b.2. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.9. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.10. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.11. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.12. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.13. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.14. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.15. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.16. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.17. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.18. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.19. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.20. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 b.7. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply Fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to RIVERVIEW 2 (523376) 69.0 kV Transmission Circuit #1 b.2. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply Fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 b.2. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply Fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to BLACKHAWK 2 (523445) 69.0 kV Transmission Circuit #1 b.2. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply Fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHERLY 2 (523526) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.2. HUTCHISON 2 (523543) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HERRING_TP 3 (523352) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to HARRNG_WST 6 (523977) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to GRAY_CNTY 3 (523636) 115.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply Fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to CAMX/AGR TP3 (523485) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to BLKHAWK_W 3 (523344) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PANTEX_N 3 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on HUTCHISON 2 (523543) 69 kV Bus a. Apply Fault at the HUTCHISON 2 (523543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.2. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.8. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.9. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.10. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-015-GEN (762463 and 762466). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G24-041-TAP 345.00 (778200) 345 kV Bus a. Apply Fault at the G24-041-TAP 345.00 (778200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-041-TAP (778200) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G24-041-TAP (778200) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.2. NICHOLS_3 1 (524023) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips A23-001-GEN (775724). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_021 | Single Phase Fault with Stuck Breaker on HARRINGTON-G1 (523977) 230 kV Bus a. Apply Fault at the HARRINGTON-G1 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to remove bus # b.5. HARRNGTON1 1 (523971) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_022 | Single Phase Fault with Stuck Breaker on HARRINGTON-G2 (523978) 230 kV Bus a. Apply Fault at the HARRINGTON-G2 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to remove bus # b.4. HARRNGTON2 1 (523972) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29W | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Base | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.2. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Woodward - Potter Co 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Base | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Woodward - Potter Co 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR16 PISIS | 29S | Base | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Woodward - Potter Co 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE_TR 1 (523265) 13.2 kV to PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EPLANT_TR3 1 (524160) 13.2 kV to EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on YARNELL_TP 3115.00 (524072) 115 kV Bus a. Apply fault at the YARNELL_TP 3115.00 (524072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.2. YARNELL_TP 3 (524072) 115.0 kV to CONWAY 3 (524079) 115.0 kV Transmission Circuit #1 b.3. CONWAY 3 (524079) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on RB-SNEED +3115.00 (523367) 115 kV Bus a. Apply fault at the RB-SNEED +3115.00 (523367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. RB-SNEED 3 (523366) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to HERRING 3 (523359) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.5. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.4. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on WHITAKER 3115.00 (524058) 115 kV Bus a. Apply fault at the WHITAKER 3115.00 (524058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. WHITAKER 3 (524058) 115.0 kV to CENTERPORT 3 (524138) 115.0 kV Transmission Circuit #1 b.3. CENTERPORT 3 (524138) 115.0 kV to EAST_PLANT 3 (524162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on CRMWA_#1TP 3115.00 (523404) 115 kV Bus a. Apply fault at the CRMWA_#1TP 3115.00 (523404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on ASARCO 3115.00 (524016) 115 kV Bus a. Apply fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on MARTIN 3115.00 (523928) 115 kV Bus a. Apply fault at the MARTIN 3115.00 (523928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on ROLLHILLS 3115.00 (524007) 115 kV Bus a. Apply fault at the ROLLHILLS 3115.00 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on Q_RYTON_TP 3115.00 (523478) 115 kV Bus a. Apply fault at the Q_RYTON_TP 3115.00 (523478) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on HERRING_TP 3115.00 (523352) 115 kV Bus a. Apply fault at the HERRING_TP 3115.00 (523352) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to ROCKYPOINT 2 (523397) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on CRMWA_#4 3115.00 (523410) 115 kV Bus a. Apply fault at the CRMWA_#4 3115.00 (523410) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on CAMX/AGR TP3115.00 (523485) 115 kV Bus a. Apply fault at the CAMX/AGR TP3115.00 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SPRINGCREEK269.000 (523512) 69 kV Bus a. Apply fault at the SPRINGCREEK269.000 (523512) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGCREEK2 (523512) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on BURNETT 269.000 (523602) 69 kV Bus a. Apply fault at the BURNETT 269.000 (523602) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURNETT 2 (523602) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on ROXANA 269.000 (523609) 69 kV Bus a. Apply fault at the ROXANA 269.000 (523609) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROXANA 2 (523609) 69.0 kV to DAMRON 2 (523616) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on DAMRON 269.000 (523616) 69 kV Bus a. Apply fault at the DAMRON 269.000 (523616) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on CRMWA#21 269.000 (523646) 69 kV Bus a. Apply fault at the CRMWA#21 269.000 (523646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#21 2 (523646) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on CRMWA#23TP 269.000 (523647) 69 kV Bus a. Apply fault at the CRMWA#23TP 269.000 (523647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#23TP 2 (523647) 69.0 kV to CRMWA#23 2 (523649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on MCCULUGH_TP269.000 (523700) 69 kV Bus a. Apply fault at the MCCULUGH_TP269.000 (523700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCULUGH_TP2 (523700) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on MIDSTRM_TP 3115.00 (523817) 115 kV Bus a. Apply fault at the MIDSTRM_TP 3115.00 (523817) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on ASARCO_TP 3115.00 (524018) 115 kV Bus a. Apply fault at the ASARCO_TP 3115.00 (524018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR11 (523710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR21 (523709) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV to GRAPEVN_TR11 (523769) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR1 1 (524361) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR2 1 (524360) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on MAJESTC_WND3115.00 (523926) 115 kV Bus a. Apply fault at the MAJESTC_WND3115.00 (523926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAJESTC_WND3 (523926) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 b.5. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply Fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 b.6. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. PRINGLE 1 (523261) 34.5 kV to PRINGLE 3 (523266) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.3. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RVRVIEW_TR11 (523375) 13.2 kV to RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV Three Winding #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 b.2. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on PANTEX_S 3115.00 (523945) 115 kV Bus a. Apply Fault at the PANTEX_S 3115.00 (523945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.2. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.3. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.4. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 b.5. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.6. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.7. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.8. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.9. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.10. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.11. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.12. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.13. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.14. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.9. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.4. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.5. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.6. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.7. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.8. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.9. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.10. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.7. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.8. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.10. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.11. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.13. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.14. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.3. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.4. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.7. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.8. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.10. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.11. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.12. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.13. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.15. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.16. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CARSON_SUB 3115.00 (523924) 115 kV Bus a. Apply Fault at the CARSON_SUB 3115.00 (523924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARSON_SUB 3 (523924) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.3. HPW_COL 1 (523920) 13.2 kV to CARSON_SUB 1 (523923) 13.2 kV Transmission Circuit #1 b.4. CARSON_SUB 1 (523923) 13.2 kV to CARSON_SUB 3 (523924) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.8. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.9. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.10. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ASARCO 3115.00 (524016) 115 kV Bus a. Apply Fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. ASARCO 3 (524016) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.6. BLACKHAWK1 1 (523461) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.5. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.6. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. BLACKHAWK2 1 (523462) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.4. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 b.5. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 b.6. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 b.7. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.3. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.2. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.3. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.4. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR21 (524042) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #2 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.5. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.8. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.9. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.3. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.9. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.10. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.11. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.12. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.6. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 b.2. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.9. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.10. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.11. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.12. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.13. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.14. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.15. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.16. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.17. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.18. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.19. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.20. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 b.7. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply Fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to RIVERVIEW 2 (523376) 69.0 kV Transmission Circuit #1 b.2. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply Fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 b.2. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply Fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to BLACKHAWK 2 (523445) 69.0 kV Transmission Circuit #1 b.2. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply Fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHERLY 2 (523526) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.2. HUTCHISON 2 (523543) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HERRING_TP 3 (523352) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to HARRNG_WST 6 (523977) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to GRAY_CNTY 3 (523636) 115.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply Fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to CAMX/AGR TP3 (523485) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to BLKHAWK_W 3 (523344) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PANTEX_N 3 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on HUTCHISON 2 (523543) 69 kV Bus a. Apply Fault at the HUTCHISON 2 (523543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.2. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.8. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.9. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.10. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G24-041-TAP 345.00 (778200) 345 kV Bus a. Apply Fault at the G24-041-TAP 345.00 (778200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-041-TAP (778200) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G24-041-TAP (778200) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.2. NICHOLS_3 1 (524023) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_021 | Single Phase Fault with Stuck Breaker on HARRINGTON-G1 (523977) 230 kV Bus a. Apply Fault at the HARRINGTON-G1 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to remove bus # b.5. HARRNGTON1 1 (523971) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_022 | Single Phase Fault with Stuck Breaker on HARRINGTON-G2 (523978) 230 kV Bus a. Apply Fault at the HARRINGTON-G2 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to remove bus # b.4. HARRNGTON2 1 (523972) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE_TR 1 (523265) 13.2 kV to PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EPLANT_TR3 1 (524160) 13.2 kV to EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on YARNELL_TP 3115.00 (524072) 115 kV Bus a. Apply fault at the YARNELL_TP 3115.00 (524072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.2. YARNELL_TP 3 (524072) 115.0 kV to CONWAY 3 (524079) 115.0 kV Transmission Circuit #1 b.3. CONWAY 3 (524079) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on RB-SNEED +3115.00 (523367) 115 kV Bus a. Apply fault at the RB-SNEED +3115.00 (523367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. RB-SNEED 3 (523366) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to HERRING 3 (523359) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.5. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.4. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on WHITAKER 3115.00 (524058) 115 kV Bus a. Apply fault at the WHITAKER 3115.00 (524058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. WHITAKER 3 (524058) 115.0 kV to CENTERPORT 3 (524138) 115.0 kV Transmission Circuit #1 b.3. CENTERPORT 3 (524138) 115.0 kV to EAST_PLANT 3 (524162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on CRMWA_#1TP 3115.00 (523404) 115 kV Bus a. Apply fault at the CRMWA_#1TP 3115.00 (523404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on ASARCO 3115.00 (524016) 115 kV Bus a. Apply fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on MARTIN 3115.00 (523928) 115 kV Bus a. Apply fault at the MARTIN 3115.00 (523928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on ROLLHILLS 3115.00 (524007) 115 kV Bus a. Apply fault at the ROLLHILLS 3115.00 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on Q_RYTON_TP 3115.00 (523478) 115 kV Bus a. Apply fault at the Q_RYTON_TP 3115.00 (523478) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to WRB_REF 3 (523214) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on PHILLIPWRBS3115.00 (523202) 115 kV Bus a. Apply fault at the PHILLIPWRBS3115.00 (523202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on HERRING_TP 3115.00 (523352) 115 kV Bus a. Apply fault at the HERRING_TP 3115.00 (523352) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to ROCKYPOINT 2 (523397) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on CRMWA_#4 3115.00 (523410) 115 kV Bus a. Apply fault at the CRMWA_#4 3115.00 (523410) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on BLACKHAWK 269.000 (523445) 69 kV Bus a. Apply fault at the BLACKHAWK 269.000 (523445) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on CAMX/AGR TP3115.00 (523485) 115 kV Bus a. Apply fault at the CAMX/AGR TP3115.00 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SPRINGCREEK269.000 (523512) 69 kV Bus a. Apply fault at the SPRINGCREEK269.000 (523512) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGCREEK2 (523512) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on W_BORGER_TP3115.00 (523516) 115 kV Bus a. Apply fault at the W_BORGER_TP3115.00 (523516) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on BURNETT 269.000 (523602) 69 kV Bus a. Apply fault at the BURNETT 269.000 (523602) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURNETT 2 (523602) 69.0 kV to CRMWA#22 2 (523623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on ROXANA 269.000 (523609) 69 kV Bus a. Apply fault at the ROXANA 269.000 (523609) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROXANA 2 (523609) 69.0 kV to DAMRON 2 (523616) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on DAMRON 269.000 (523616) 69 kV Bus a. Apply fault at the DAMRON 269.000 (523616) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on CRMWA#21 269.000 (523646) 69 kV Bus a. Apply fault at the CRMWA#21 269.000 (523646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#21 2 (523646) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on CRMWA#23TP 269.000 (523647) 69 kV Bus a. Apply fault at the CRMWA#23TP 269.000 (523647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRMWA#23TP 2 (523647) 69.0 kV to CRMWA#23 2 (523649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on MCCULUGH_TP269.000 (523700) 69 kV Bus a. Apply fault at the MCCULUGH_TP269.000 (523700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCULUGH_TP2 (523700) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on MIDSTRM_TP 3115.00 (523817) 115 kV Bus a. Apply fault at the MIDSTRM_TP 3115.00 (523817) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on ASARCO_TP 3115.00 (524018) 115 kV Bus a. Apply fault at the ASARCO_TP 3115.00 (524018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR11 (523710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on KINGSMILL 3115.00 (523712) 115 kV Bus a. Apply fault at the KINGSMILL 3115.00 (523712) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINGSMILL 3 (523712) 115.0 kV to KINGSMILL 2 (523711) 69.0 kV to KNGSMIL_TR21 (523709) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV to GRAPEVN_TR11 (523769) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR1 1 (524361) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR2 1 (524360) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERVIEW 2 (523376) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on HUTCHISON 269.000 (523543) 69 kV Bus a. Apply fault at the HUTCHISON 269.000 (523543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 2 (523543) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on GRAY_CNTY 269.000 (523635) 69 kV Bus a. Apply fault at the GRAY_CNTY 269.000 (523635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on MAJESTC_WND3115.00 (523926) 115 kV Bus a. Apply fault at the MAJESTC_WND3115.00 (523926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAJESTC_WND3 (523926) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.2. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 b.5. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply Fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 b.6. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. PRINGLE 1 (523261) 34.5 kV to PRINGLE 3 (523266) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.2. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.3. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RVRVIEW_TR11 (523375) 13.2 kV to RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV Three Winding #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on PANTEX_N 3115.00 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3115.00 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTIN 3 (523928) 115.0 kV to PANTEX_N 3 (523938) 115.0 kV Transmission Circuit #1 b.2. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on PANTEX_S 3115.00 (523945) 115 kV Bus a. Apply Fault at the PANTEX_S 3115.00 (523945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.2. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.3. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.4. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 b.5. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.6. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.7. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.8. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.9. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.10. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.11. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.12. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.13. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.14. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.8. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.9. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3115.00 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3115.00 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 b.4. HIGHLAND_TP3 (523931) 115.0 kV to HIGHLAND 3 (524065) 115.0 kV Transmission Circuit #1 b.5. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 b.6. PANTEX_S 1 (523933) 12.5 kV to PANTEXWND 1 (523934) 34.5 kV Two Winding #1 b.7. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #1 b.8. PANTEX_S 3 (523945) 115.0 kV to PANTEX_S 1 (523933) 12.5 kV Two Winding #2 b.9. PANTEXWNDCC1 (523935) 34.5 kV to PANTEX_WIND1 (523936) 0.7 kV Two Winding #1 b.10. PANTEXWND 1 (523934) 34.5 kV to PANTEXWNDCC1 (523935) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.7. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.8. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.10. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.11. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.13. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.14. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.3. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.4. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.5. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 b.6. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 b.7. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.8. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.9. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.10. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.11. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.12. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.13. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.15. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.16. PHILLIPWRBS3 (523202) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CARSON_SUB 3115.00 (523924) 115 kV Bus a. Apply Fault at the CARSON_SUB 3115.00 (523924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARSON_SUB 3 (523924) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.3. HPW_COL 1 (523920) 13.2 kV to CARSON_SUB 1 (523923) 13.2 kV Transmission Circuit #1 b.4. CARSON_SUB 1 (523923) 13.2 kV to CARSON_SUB 3 (523924) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.3. W_BORGER_TP3 (523516) 115.0 kV to W_BORGER 3 (523518) 115.0 kV Transmission Circuit #1 b.4. CAMX/AGR TP3 (523485) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. CAMX/AGR TP3 (523485) 115.0 kV to CAMEX/AGRM 3 (523486) 115.0 kV Transmission Circuit #1 b.6. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.7. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.8. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.9. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.10. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ASARCO 3115.00 (524016) 115 kV Bus a. Apply Fault at the ASARCO 3115.00 (524016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. ASARCO 3 (524016) 115.0 kV to ASARCO_TP 3 (524018) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK1 113.800 (523461) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK1 1 (523461) 13.8 kV Two Winding #1 b.3. BLKHAWK_TR11 (523341) 13.2 kV to BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.5. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.6. BLACKHAWK1 1 (523461) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus a. Apply Fault at the BLACKHAWK2 113.800 (523462) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_TR21 (523342) 13.2 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV Three Winding #1 b.3. BLKHAWK_W 3 (523344) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_E 3 (523346) 115.0 kV to BLACKHAWK2 1 (523462) 13.8 kV Two Winding #1 b.5. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.6. BLKHAWK_E 3 (523346) 115.0 kV to CPCOKER 3 (523470) 115.0 kV Transmission Circuit #1 b.7. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.8. BLACKHAWK2 1 (523462) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.4. DAMRON 2 (523616) 69.0 kV to GRAY_CNTY 2 (523635) 69.0 kV Transmission Circuit #1 b.5. GRAY_CNTY 2 (523635) 69.0 kV to CRMWA#23TP 2 (523647) 69.0 kV Transmission Circuit #1 b.6. GRAY_CNTY 2 (523635) 69.0 kV to KITE 2 (523653) 69.0 kV Transmission Circuit #1 b.7. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.4. HARRNG_MID 6 (523978) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_MID 6 (523978) 230.0 kV to HARRNGTON2 1 (523972) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to HARRNG_MID 6 (523978) 230.0 kV Transmission Circuit #@1 b.5. HARRNG_WST 6 (523977) 230.0 kV to HARRNGTON1 1 (523971) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.7. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.8. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.7. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.3. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.5. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.2. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.3. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.4. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR3 1 (523542) 13.2 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV Three Winding #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.4. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.7. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_N 3 (523544) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.4. HUTCH_N 3 (523544) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #@1 b.5. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 2 (523543) 69.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.6. HUTCH_S 3 (523546) 115.0 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR1N 1 (523540) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_TR2S 1 (523541) 13.2 kV to HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV Three Winding #1 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to HUTCH_N 3 (523544) 115.0 kV to HUTCH_TR1N 1 (523540) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.2. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.3. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.4. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.2. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.3. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.4. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.5. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.6. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.7. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.8. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.9. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.10. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.11. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MOORE_E 3115.00 (523308) 115 kV Bus a. Apply Fault at the MOORE_E 3115.00 (523308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ETTER 3 (523256) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. DUMAS_19ST 3 (523318) 115.0 kV to DEMON_TP 3 (523319) 115.0 kV Transmission Circuit #1 b.3. RB-HOGUE 3 (523216) 115.0 kV to DALHART 3 (523246) 115.0 kV Transmission Circuit #1 b.4. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.6. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.7. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.8. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.9. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 b.10. MOORE_TR1 1 (523302) 13.2 kV to MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Three Winding #1 b.11. EW9_COL 1 (523296) 12.5 kV to EW9_GEN 1 (523297) 0.6 kV Two Winding #1 b.12. EW9SP2 1 (523294) 12.5 kV to MOORE_E 1 (523301) 12.5 kV Transmission Circuit #1 b.13. MOORE_E 1 (523301) 12.5 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #1 b.14. VALERO 3 (523277) 115.0 kV to MOORE_W 3 (523304) 115.0 kV Transmission Circuit #1 b.15. VALERO 3 (523277) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR21 (524042) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #2 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.5. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.6. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.7. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.8. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.9. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.3. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.7. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.9. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.10. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.11. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.12. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NICHOLS_2 113.800 (524022) 13.80000019 kV Bus a. Apply Fault at the NICHOLS_2 113.800 (524022) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. NICHOLS_1 1 (524021) 13.8 kV to Generator #1 b.6. NICHOLS_2 1 (524022) 13.8 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on NICHOLS 3115.00 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3115.00 (524043) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGSMILL 3 (523712) 115.0 kV to TYNG 3 (523721) 115.0 kV Transmission Circuit #1 b.2. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.3. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on NICHOLS_3 122.000 (524023) 22 kV Bus a. Apply Fault at the NICHOLS_3 122.000 (524023) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS_3 1 (524023) 22.0 kV Two Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. NICHOLS_3 1 (524023) 22.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.2. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. HIGHLAND_TP3 (523931) 115.0 kV to PANTEX_S 3 (523945) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.3. CRMWA_#3 3 (523407) 115.0 kV to MEREDITH 3 (523494) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#3 3 (523407) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#2 3 (523405) 115.0 kV to FRITCH 3 (523492) 115.0 kV Transmission Circuit #1 b.6. CRMWA_#1TP 3 (523404) 115.0 kV to CRMWA_#2 3 (523405) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.8. CRMWA_#1 3 (523403) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.9. NICHOLS_TR11 (524041) 13.2 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV Three Winding #1 b.10. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.11. MIDSTRM_TP 3 (523817) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.12. ROLLHILLS 3 (524007) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.13. ASARCO 3 (524016) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.14. ASARCO_TP 3 (524018) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.15. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.16. NICHOLS 3 (524043) 115.0 kV to YARNELL_TP 3 (524072) 115.0 kV Transmission Circuit #1 b.17. NICHOLS 3 (524043) 115.0 kV to NICHOLS_1 1 (524021) 13.8 kV Two Winding #1 b.18. NICHOLS 3 (524043) 115.0 kV to NICHOLS_2 1 (524022) 13.8 kV Two Winding #1 b.19. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.20. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PHILLIPWRBS3 (523202) 115.0 kV to BLKHAWK_E 3 (523346) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 b.5. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.2. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.2. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.7. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.3. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.4. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.2. HERRING_TP 3 (523352) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.3. RIVERVIEW 3 (523377) 115.0 kV to CRMWA_#1TP 3 (523404) 115.0 kV Transmission Circuit #1 b.4. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 b.5. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 3 (523377) 115.0 kV to RIVERVIEW 2 (523376) 69.0 kV to RVRVIEW_TR11 (523375) 13.2 kV Three Winding #1 b.7. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. CRMWA_#4 3 (523410) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 b.3. CAMX/AGR TP3 (523485) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.4. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 b.5. MOORE_W 3 (523304) 115.0 kV to RB-SNEED +3 (523367) 115.0 kV Transmission Circuit #1 b.6. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.7. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on INDUSTRIAL 269.000 (523413) 69 kV Bus a. Apply Fault at the INDUSTRIAL 269.000 (523413) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDUSTRIAL 2 (523413) 69.0 kV to RIVERVIEW 2 (523376) 69.0 kV Transmission Circuit #1 b.2. INDUSTRIAL 2 (523413) 69.0 kV to CAMEX/TRNSP2 (523484) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CAMEX/TRNSP269.000 (523484) 69 kV Bus a. Apply Fault at the CAMEX/TRNSP269.000 (523484) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMEX/TRNSP2 (523484) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 b.2. CAMEX/TRNSP2 (523484) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on PHILLPREF2 269.000 (523505) 69 kV Bus a. Apply Fault at the PHILLPREF2 269.000 (523505) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILLPREF2 2 (523505) 69.0 kV to BLACKHAWK 2 (523445) 69.0 kV Transmission Circuit #1 b.2. PHILLPREF2 2 (523505) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WEATHERLY 269.000 (523526) 69 kV Bus a. Apply Fault at the WEATHERLY 269.000 (523526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEATHERLY 2 (523526) 69.0 kV to PHILLPREF2 2 (523505) 69.0 kV Transmission Circuit #1 b.2. WEATHERLY 2 (523526) 69.0 kV to HUTCHISON 2 (523543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR3 1 (523542) 13.2 kV Three Winding #1 b.2. HUTCHISON 2 (523543) 69.0 kV to WEATHERLY 2 (523526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on BLKHAWK_W 3115.00 (523344) 115 kV Bus a. Apply Fault at the BLKHAWK_W 3115.00 (523344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKHAWK_W 3 (523344) 115.0 kV to HUTCH_N 3 (523544) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_W 3 (523344) 115.0 kV to BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_TR11 (523341) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on RIVERVIEW 3115.00 (523377) 115 kV Bus a. Apply Fault at the RIVERVIEW 3115.00 (523377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 3 (523377) 115.0 kV to HERRING_TP 3 (523352) 115.0 kV Transmission Circuit #1 b.2. RIVERVIEW 3 (523377) 115.0 kV to W_BORGER_TP3 (523516) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HUTCH_S 3115.00 (523546) 115 kV Bus a. Apply Fault at the HUTCH_S 3115.00 (523546) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_S 3 (523546) 115.0 kV to MARTIN 3 (523928) 115.0 kV Transmission Circuit #1 b.2. HUTCH_S 3 (523546) 115.0 kV to GRAY_CNTY 3 (523636) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. HUTCHISON 6 (523551) 230.0 kV to HUTCH_S 3 (523546) 115.0 kV to HUTCH_TR2S 1 (523541) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 3 (523636) 115.0 kV to HUTCH_S 3 (523546) 115.0 kV Transmission Circuit #1 b.2. GRAY_CNTY 3 (523636) 115.0 kV to GRAY_CNTY 2 (523635) 69.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. NICHOLS 6 (524044) 230.0 kV to HARRNG_WST 6 (523977) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRAY_CNTY 3115.00 (523636) 115 kV Bus a. Apply Fault at the GRAY_CNTY 3115.00 (523636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAY_CNTY 2 (523635) 69.0 kV to GRAY_CNTY 3 (523636) 115.0 kV to GRAYCO_TR1 1 (523634) 13.2 kV Three Winding #1 b.2. GRAY_CNTY 2 (523635) 69.0 kV to KINGSMILL 2 (523711) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BLKHAWK_E 3115.00 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3115.00 (523346) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 2 (523445) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. BLACKHAWK 2 (523445) 69.0 kV to BLKHAWK_E 3 (523346) 115.0 kV to BLKHAWK_TR21 (523342) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on RIVERVIEW 269.000 (523376) 69 kV Bus a. Apply Fault at the RIVERVIEW 269.000 (523376) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERVIEW 2 (523376) 69.0 kV to PHILLPREF1 2 (523498) 69.0 kV Transmission Circuit #1 b.2. RIVERVIEW 2 (523376) 69.0 kV to INDUSTRIAL 2 (523413) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on HUTCH_N 3115.00 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3115.00 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to CAMX/AGR TP3 (523485) 115.0 kV Transmission Circuit #1 b.2. HUTCH_N 3 (523544) 115.0 kV to BLKHAWK_W 3 (523344) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 3 (524043) 115.0 kV to WHITAKER 3 (524058) 115.0 kV Transmission Circuit #1 b.2. NICHOLS 3 (524043) 115.0 kV to NICHOLS 6 (524044) 230.0 kV to NICHOLS_TR21 (524042) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PANTEX_N 3 (523938) 115 kV Bus a. Apply Fault at the PANTEX_N 3 (523938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PANTEX_N 3 (523938) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HIGHLAND_TP3 (523931) 115 kV Bus a. Apply Fault at the HIGHLAND_TP3 (523931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLAND_TP3 (523931) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCH_N 3 (523544) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on HUTCHISON 2 (523543) 69 kV Bus a. Apply Fault at the HUTCHISON 2 (523543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 2 (523543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUTCHISON 6 (523551) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.2. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Phantom 765 kV Line Reactor Potter Co 765 kV Line Reactor
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.8. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.9. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.10. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to GRAPEVINE 6 (523771) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G24-041-TAP 345.00 (778200) 345 kV Bus a. Apply Fault at the G24-041-TAP 345.00 (778200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-041-TAP (778200) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G24-041-TAP (778200) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Phantom 765 kV Line Reactor Potter Co 765 kV Line Reactor
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.2. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230 kV Bus a. Apply Fault at the NICHOLS (524044) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 b.2. NICHOLS_3 1 (524023) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | Phantom 765 kV Line Reactor Potter Co 765 kV Line Reactor
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_021 | Single Phase Fault with Stuck Breaker on HARRINGTON-G1 (523977) 230 kV Bus a. Apply Fault at the HARRINGTON-G1 (523977) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 b.2. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 b.3. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to remove bus # b.5. HARRNGTON1 1 (523971) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_022 | Single Phase Fault with Stuck Breaker on HARRINGTON-G2 (523978) 230 kV Bus a. Apply Fault at the HARRINGTON-G2 (523978) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 b.2. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 b.3. HARRNG_MID 6 (523978) 230.0 kV to remove bus # b.4. HARRNGTON2 1 (523972) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29S | Base | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Base | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.2. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Phantom 765 kV Line Reactor Potter Co 765 kV Line Reactor
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Base | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Base | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Phantom 765 kV Line Reactor Potter Co 765 kV Line Reactor
05 SOUTHWEST | GEN-2026-PR16 PISIS CF | 29W | Base | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at multiple generator sites including Tolk (525561 and 525562) and Elk (525844, 525845 and 525846) generating sites in post fault conditions. | Phantom 765 kV Line Reactor Potter Co 765 kV Line Reactor

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 29SP Fault Current 3-Phase (kA) | Request In Service 29SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR16 | 05 SOUTHWEST | 923928 | HIGH_MAJE_HV | 115 | 6.7781 | 6.9912 | 0.2131
GEN-2026-PR16 | 05 SOUTHWEST | 523928 | MARTIN 3 | 115 | 7.9156 | 8.1278 | 0.2122
GEN-2026-PR16 | 05 SOUTHWEST | 523924 | CARSON_SUB 3 | 115 | 7.0635 | 7.2318 | 0.1683
GEN-2026-PR16 | 05 SOUTHWEST | 523926 | MAJESTC_WND3 | 115 | 7.0275 | 7.1877 | 0.1602
GEN-2026-PR16 | 05 SOUTHWEST | 523938 | PANTEX_N 3 | 115 | 7.9571 | 8.0904 | 0.1333
GEN-2026-PR16 | 05 SOUTHWEST | 523945 | PANTEX_S 3 | 115 | 8.5245 | 8.629 | 0.1045
GEN-2026-PR16 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 33.5701 | 33.645 | 0.0749
GEN-2026-PR16 | 05 SOUTHWEST | 524018 | ASARCO_TP 3 | 115 | 31.3026 | 31.3758 | 0.0732
GEN-2026-PR16 | 05 SOUTHWEST | 523931 | HIGHLAND_TP3 | 115 | 12.1307 | 12.2029 | 0.0722
GEN-2026-PR16 | 05 SOUTHWEST | 523544 | HUTCH_N 3 | 115 | 17.2501 | 17.3125 | 0.0624
GEN-2026-PR16 | 05 SOUTHWEST | 523546 | HUTCH_S 3 | 115 | 17.2501 | 17.3125 | 0.0624
GEN-2026-PR16 | 05 SOUTHWEST | 524016 | ASARCO 3 | 115 | 28.861 | 28.9157 | 0.0547
GEN-2026-PR16 | 05 SOUTHWEST | 523485 | CAMX/AGR TP3 | 115 | 15.3012 | 15.3475 | 0.0463
GEN-2026-PR16 | 05 SOUTHWEST | 523486 | CAMEX/AGRM 3 | 115 | 14.0611 | 14.1003 | 0.0392
GEN-2026-PR16 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 30.977 | 31.0122 | 0.0352
GEN-2026-PR16 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 30.977 | 31.0122 | 0.0352
GEN-2026-PR16 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 30.977 | 31.0122 | 0.0352
GEN-2026-PR16 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 29.797 | 29.832 | 0.035
GEN-2026-PR16 | 05 SOUTHWEST | 523516 | W_BORGER_TP3 | 115 | 13.4301 | 13.4605 | 0.0304
GEN-2026-PR16 | 05 SOUTHWEST | 523377 | RIVERVIEW 3 | 115 | 14.628 | 14.6572 | 0.0292
GEN-2026-PR16 | 05 SOUTHWEST | 524058 | WHITAKER 3 | 115 | 23.736 | 23.7646 | 0.0286
GEN-2026-PR16 | 05 SOUTHWEST | 524065 | HIGHLAND 3 | 115 | 6.3405 | 6.3601 | 0.0196
GEN-2026-PR16 | 05 SOUTHWEST | 523518 | W_BORGER 3 | 115 | 10.4934 | 10.512 | 0.0186
GEN-2026-PR16 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 23.523 | 23.5409 | 0.0179
GEN-2026-PR16 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 21.2928 | 21.3092 | 0.0164
GEN-2026-PR16 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 20.3221 | 20.3371 | 0.015
GEN-2026-PR16 | 05 SOUTHWEST | 523344 | BLKHAWK_W 3 | 115 | 13.2517 | 13.2649 | 0.0132
GEN-2026-PR16 | 05 SOUTHWEST | 523346 | BLKHAWK_E 3 | 115 | 13.2517 | 13.2649 | 0.0132
GEN-2026-PR16 | 05 SOUTHWEST | 523470 | CPCOKER 3 | 115 | 13.1311 | 13.144 | 0.0129
GEN-2026-PR16 | 05 SOUTHWEST | 523202 | PHILLIPWRBS3 | 115 | 13.047 | 13.0597 | 0.0127
GEN-2026-PR16 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.803 | 7.8148 | 0.0118
GEN-2026-PR16 | 05 SOUTHWEST | 523478 | Q_RYTON_TP 3 | 115 | 12.6249 | 12.6367 | 0.0118
GEN-2026-PR16 | 05 SOUTHWEST | 523214 | WRB_REF 3 | 115 | 12.5358 | 12.5475 | 0.0117
GEN-2026-PR16 | 05 SOUTHWEST | 524163 | EAST_PLANT 6 | 230 | 15.2454 | 15.255 | 0.0096
GEN-2026-PR16 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 15.9537 | 15.9632 | 0.0095
GEN-2026-PR16 | 05 SOUTHWEST | 523445 | BLACKHAWK 2 | 69 | 13.6687 | 13.6779 | 0.0092
GEN-2026-PR16 | 05 SOUTHWEST | 523410 | CRMWA_#4 3 | 115 | 10.3563 | 10.3645 | 0.0082
GEN-2026-PR16 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.8763 | 14.8842 | 0.0079
GEN-2026-PR16 | 05 SOUTHWEST | 523404 | CRMWA_#1TP 3 | 115 | 8.0879 | 8.0957 | 0.0078
GEN-2026-PR16 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 18.2228 | 18.2305 | 0.0077
GEN-2026-PR16 | 05 SOUTHWEST | 523405 | CRMWA_#2 3 | 115 | 7.9976 | 8.0052 | 0.0076
GEN-2026-PR16 | 05 SOUTHWEST | 523543 | HUTCHISON 2 | 69 | 11.0726 | 11.0799 | 0.0073
GEN-2026-PR16 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 12.1278 | 12.1343 | 0.0065
GEN-2026-PR16 | 05 SOUTHWEST | 523492 | FRITCH 3 | 115 | 7.4312 | 7.4375 | 0.0063
GEN-2026-PR16 | 05 SOUTHWEST | 523484 | CAMEX/TRNSP2 | 69 | 10.6984 | 10.7046 | 0.0062
GEN-2026-PR16 | 05 SOUTHWEST | 523376 | RIVERVIEW 2 | 69 | 10.5819 | 10.5878 | 0.0059
GEN-2026-PR16 | 05 SOUTHWEST | 523505 | PHILLPREF2 2 | 69 | 10.6151 | 10.6209 | 0.0058
GEN-2026-PR16 | 05 SOUTHWEST | 523498 | PHILLPREF1 2 | 69 | 10.546 | 10.5517 | 0.0057
GEN-2026-PR16 | 05 SOUTHWEST | 523413 | INDUSTRIAL 2 | 69 | 10.9611 | 10.9668 | 0.0057
GEN-2026-PR16 | 05 SOUTHWEST | 523403 | CRMWA_#1 3 | 115 | 6.7669 | 6.7724 | 0.0055
GEN-2026-PR16 | 05 SOUTHWEST | 523623 | CRMWA#22 2 | 69 | 9.4712 | 9.4765 | 0.0053
GEN-2026-PR16 | 05 SOUTHWEST | 523526 | WEATHERLY 2 | 69 | 9.3305 | 9.3354 | 0.0049
GEN-2026-PR16 | 05 SOUTHWEST | 523352 | HERRING_TP 3 | 115 | 7.623 | 7.6279 | 0.0049
GEN-2026-PR16 | 05 SOUTHWEST | 524072 | YARNELL_TP 3 | 115 | 8.467 | 8.471 | 0.004
GEN-2026-PR16 | 05 SOUTHWEST | 523431 | SIDRICHARD 2 | 69 | 9.2389 | 9.2426 | 0.0037
GEN-2026-PR16 | 05 SOUTHWEST | 523421 | HUBER_GEN 2 | 69 | 8.9597 | 8.9633 | 0.0036
GEN-2026-PR16 | 05 SOUTHWEST | 523304 | MOORE_W 3 | 115 | 14.1182 | 14.1217 | 0.0035
GEN-2026-PR16 | 05 SOUTHWEST | 523366 | RB-SNEED 3 | 115 | 7.1842 | 7.1873 | 0.0031
GEN-2026-PR16 | 05 SOUTHWEST | 523367 | RB-SNEED +3 | 115 | 7.1953 | 7.1984 | 0.0031
GEN-2026-PR16 | 05 SOUTHWEST | 523339 | FAIN 3 | 115 | 9.2165 | 9.2188 | 0.0023
GEN-2026-PR16 | 05 SOUTHWEST | 523359 | HERRING 3 | 115 | 5.2095 | 5.2118 | 0.0023
GEN-2026-PR16 | 05 SOUTHWEST | 523636 | GRAY_CNTY 3 | 115 | 4.109 | 4.1112 | 0.0022
GEN-2026-PR16 | 05 SOUTHWEST | 523186 | SPEARMAN 3 | 115 | 9.528 | 9.5301 | 0.0021
GEN-2026-PR16 | 05 SOUTHWEST | 523770 | GRAPEVINE 3 | 115 | 9.5286 | 9.5306 | 0.002
GEN-2026-PR16 | 05 SOUTHWEST | 523602 | BURNETT 2 | 69 | 5.6318 | 5.6337 | 0.0019
GEN-2026-PR16 | 05 SOUTHWEST | 523711 | KINGSMILL 2 | 69 | 8.6902 | 8.6921 | 0.0019
GEN-2026-PR16 | 05 SOUTHWEST | 523397 | ROCKYPOINT 2 | 69 | 5.7161 | 5.7178 | 0.0017
GEN-2026-PR16 | 05 SOUTHWEST | 523635 | GRAY_CNTY 2 | 69 | 6.3375 | 6.3391 | 0.0016
GEN-2026-PR16 | 05 SOUTHWEST | 523712 | KINGSMILL 3 | 115 | 6.9292 | 6.9307 | 0.0015
GEN-2026-PR16 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.6156 | 4.617 | 0.0014
GEN-2026-PR16 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 6.4192 | 6.4204 | 0.0012
GEN-2026-PR16 | 05 SOUTHWEST | 523817 | MIDSTRM_TP 3 | 115 | 5.5887 | 5.5899 | 0.0012
GEN-2026-PR16 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.7922 | 6.7933 | 0.0011
GEN-2026-PR16 | 05 SOUTHWEST | 523700 | MCCULUGH_TP2 | 69 | 6.925 | 6.926 | 0.001
GEN-2026-PR16 | 05 SOUTHWEST | 523653 | KITE 2 | 69 | 4.4907 | 4.4916 | 0.0009
GEN-2026-PR16 | 05 SOUTHWEST | 523195 | HANSFORD 3 | 115 | 11.079 | 11.0799 | 0.0009
GEN-2026-PR16 | 05 SOUTHWEST | 523203 | SPEARMNSUB 3 | 115 | 6.5957 | 6.5965 | 0.0008
GEN-2026-PR16 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2512 | 11.252 | 0.0008
GEN-2026-PR16 | 05 SOUTHWEST | 523701 | MCCULLOUGH 2 | 69 | 4.8965 | 4.897 | 0.0005
GEN-2026-PR16 | 05 SOUTHWEST | 523616 | DAMRON 2 | 69 | 3.3114 | 3.3119 | 0.0005
GEN-2026-PR16 | 05 SOUTHWEST | 523777 | WHEELER 6 | 230 | 6.5522 | 6.5527 | 0.0005
GEN-2026-PR16 | 05 SOUTHWEST | 523185 | SPEARMAN 2 | 69 | 4.4193 | 4.4196 | 0.0003
GEN-2026-PR16 | 05 SOUTHWEST | 523609 | ROXANA 2 | 69 | 2.717 | 2.7173 | 0.0003
GEN-2026-PR16 | 05 SOUTHWEST | 523209 | NP-69_12_TP2 | 69 | 4.3782 | 4.3784 | 0.0002
GEN-2026-PR16 | 05 SOUTHWEST | 523647 | CRMWA#23TP 2 | 69 | 2.4313 | 2.4315 | 0.0002
GEN-2026-PR16 | 05 SOUTHWEST | 523143 | NP-PERDUR_G3 | 115 | 2.79 | 2.7902 | 0.0002
GEN-2026-PR16 | 05 SOUTHWEST | 523144 | NP-PERDURE 3 | 115 | 2.4935 | 2.4937 | 0.0002
GEN-2026-PR16 | 05 SOUTHWEST | 523153 | NP-OCHILTRE3 | 115 | 2.1394 | 2.1396 | 0.0002
GEN-2026-PR16 | 05 SOUTHWEST | 523646 | CRMWA#21 2 | 69 | 2.4205 | 2.4207 | 0.0002
GEN-2026-PR16 | 05 SOUTHWEST | 523208 | NP-SPEARMAN2 | 69 | 2.639 | 2.6391 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523210 | NP-GRUVER 2 | 69 | 2.2891 | 2.2892 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523662 | LYONS_TP 2 | 69 | 2.4816 | 2.4817 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523139 | NP_SPER2_TP2 | 69 | 1.8665 | 1.8666 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523152 | NP-OCHILTRE2 | 69 | 1.8722 | 1.8723 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523182 | NP-PERYTN_G2 | 69 | 1.4217 | 1.4218 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523188 | NP-LUCKY_G 2 | 69 | 1.5475 | 1.5476 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523194 | NP-VALERO-G2 | 69 | 1.539 | 1.5391 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523649 | CRMWA#23 2 | 69 | 1.4902 | 1.4903 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523138 | NP_SPER1_TP2 | 69 | 3.1886 | 3.1887 | 0.0001
GEN-2026-PR16 | 05 SOUTHWEST | 523136 | NP-HARBOUR 2 | 69 | 2.1475 | 2.1475 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523137 | NP-SUB_A 2 | 69 | 1.0607 | 1.0607 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523178 | NP-LIPS_SHA2 | 69 | 0.5985 | 0.5985 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523179 | NP-LIPSCOMB2 | 69 | 0.5981 | 0.5981 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523180 | NP-BOOKER 2 | 69 | 0.9472 | 0.9472 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523181 | NP-PERRYTON2 | 69 | 1.3965 | 1.3965 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523187 | NP-SHATTUCK2 | 69 | 0.5393 | 0.5393 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523189 | NP-LUCKY_CR2 | 69 | 1.546 | 1.546 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523190 | NP-ROGER_SP2 | 69 | 1.2549 | 1.2549 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523192 | NP-GLAZIR_G2 | 69 | 0.74 | 0.74 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523193 | NP-VALERO_P2 | 69 | 0.6239 | 0.6239 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523204 | NP-ROGERS-G2 | 69 | 1.1186 | 1.1186 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523205 | NP-ROGERS 2 | 69 | 1.0332 | 1.0332 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523206 | NP-LEWIE_G 2 | 69 | 1.6911 | 1.6911 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523207 | NP-LEWIE 2 | 69 | 1.57 | 1.57 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523512 | SPRINGCREEK2 | 69 | 1.607 | 1.607 | 0
GEN-2026-PR16 | 05 SOUTHWEST | 523683 | LYONS 2 | 69 | 2.0641 | 2.0641 | 0

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
05 SOUTHWEST | GEN-2026-PR16 | 16.301 | PASS | 0.4122 | PASS | N/A | N/A | No

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | BASE CASE | 31.8679 | PASS | 0.41249 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | BASE CASE | 31.8407 | PASS | 0.41221 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524415 [AMA_SOUTH 6 230.00] TO BUS 525213 [SWISHER 6 230.00] CKT 1 | 31.7789 | PASS | 0.41222 | PASS | 312.2217 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524415 [AMA_SOUTH 6 230.00] TO BUS 525213 [SWISHER 6 230.00] CKT 1 | 31.8064 | PASS | 0.4125 | PASS | 312.5043 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524415 [AMA_SOUTH 6 230.00] TO BUS 524414 [AMA_SOUTH 3 115.00] CKT 1 | 31.8376 | PASS | 0.4122 | PASS | 312.2035 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524415 [AMA_SOUTH 6 230.00] TO BUS 524414 [AMA_SOUTH 3 115.00] CKT 1 | 31.8757 | PASS | 0.41248 | PASS | 312.4821 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524415 [AMA_SOUTH 6 230.00] TO BUS 524365 [RANDALL 6 230.00] CKT 1 | 31.8378 | PASS | 0.41221 | PASS | 312.2071 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524415 [AMA_SOUTH 6 230.00] TO BUS 524365 [RANDALL 6 230.00] CKT 1 | 31.8642 | PASS | 0.41249 | PASS | 312.4886 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524044 [NICHOLS 6 230.00] TO BUS 524415 [AMA_SOUTH 6 230.00] CKT 1 | 31.84 | PASS | 0.41221 | PASS | 312.2065 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524044 [NICHOLS 6 230.00] TO BUS 524415 [AMA_SOUTH 6 230.00] CKT 1 | 31.867 | PASS | 0.41249 | PASS | 312.488 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524044 [NICHOLS 6 230.00] TO BUS 524023 [NICHOLS_3 1 22.00] CKT 1 | 31.6715 | PASS | 0.41224 | PASS | 312.2397 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524044 [NICHOLS 6 230.00] TO BUS 524023 [NICHOLS_3 1 22.00] CKT 1 | 31.705 | PASS | 0.41251 | PASS | 312.5117 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524079 [CONWAY 3 115.00] CKT 1 | 31.807 | PASS | 0.41223 | PASS | 312.2301 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524079 [CONWAY 3 115.00] CKT 1 | 31.827 | PASS | 0.41252 | PASS | 312.5151 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524058 [WHITAKER 3 115.00] CKT 1 | 31.6389 | PASS | 0.4123 | PASS | 312.2973 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524058 [WHITAKER 3 115.00] CKT 1 | 31.6656 | PASS | 0.4126 | PASS | 312.6023 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 2 | 31.6246 | PASS | 0.41226 | PASS | 312.2614 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 2 | 31.6265 | PASS | 0.41257 | PASS | 312.5654 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 31.6243 | PASS | 0.41226 | PASS | 312.2614 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 31.6264 | PASS | 0.41257 | PASS | 312.5654 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524022 [NICHOLS_2 1 13.8.00] CKT 1 | 31.4943 | PASS | 0.4123 | PASS | 312.3011 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524022 [NICHOLS_2 1 13.8.00] CKT 1 | 31.5672 | PASS | 0.41256 | PASS | 312.5644 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524021 [NICHOLS_1 1 13.8.00] CKT 1 | 31.506 | PASS | 0.4123 | PASS | 312.2952 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524021 [NICHOLS_1 1 13.8.00] CKT 1 | 31.5751 | PASS | 0.41256 | PASS | 312.5602 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524016 [ASARCO 3 115.00] CKT 1 | 31.8413 | PASS | 0.41221 | PASS | 312.2063 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524016 [ASARCO 3 115.00] CKT 1 | 31.8685 | PASS | 0.41249 | PASS | 312.4875 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524007 [ROLLHILLS 3 115.00] CKT 1 | 31.7007 | PASS | 0.41227 | PASS | 312.2676 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 524007 [ROLLHILLS 3 115.00] CKT 1 | 31.7284 | PASS | 0.41256 | PASS | 312.5639 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 523817 [MIDSTRM_TP 3 115.00] CKT 1 | 31.8212 | PASS | 0.41224 | PASS | 312.2371 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 523817 [MIDSTRM_TP 3 115.00] CKT 1 | 31.8465 | PASS | 0.41252 | PASS | 312.5191 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 523410 [CRMWA_#4 3 115.00] CKT 1 | 31.7735 | PASS | 0.41222 | PASS | 312.2215 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 523410 [CRMWA_#4 3 115.00] CKT 1 | 31.8042 | PASS | 0.41249 | PASS | 312.4924 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 523339 [FAIN 3 115.00] CKT 1 | 31.7756 | PASS | 0.41224 | PASS | 312.2357 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524043 [NICHOLS 3 115.00] TO BUS 523339 [FAIN 3 115.00] CKT 1 | 31.7997 | PASS | 0.41253 | PASS | 312.5259 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524018 [ASARCO_TP 3 115.00] TO BUS 524043 [NICHOLS 3 115.00] CKT 1 | 31.1281 | PASS | Not Converged | PASS | 0 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 524018 [ASARCO_TP 3 115.00] TO BUS 524043 [NICHOLS 3 115.00] CKT 1 | 17.0745 | PASS | 0.4206 | PASS | 320.5961 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523978 [HARRNG_MID 6 230.00] TO BUS 524365 [RANDALL 6 230.00] CKT 1 | 31.8429 | PASS | 0.4122 | PASS | 312.2049 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523978 [HARRNG_MID 6 230.00] TO BUS 524365 [RANDALL 6 230.00] CKT 1 | 31.8723 | PASS | 0.41248 | PASS | 312.4849 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523978 [HARRNG_MID 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 2 | 31.8197 | PASS | 0.41221 | PASS | 312.2101 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523978 [HARRNG_MID 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 2 | 31.8472 | PASS | 0.41249 | PASS | 312.4924 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523978 [HARRNG_MID 6 230.00] TO BUS 523972 [HARRNGTON2 1 24.00] CKT 1 | 31.6642 | PASS | 0.41223 | PASS | 312.2281 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523978 [HARRNG_MID 6 230.00] TO BUS 523972 [HARRNGTON2 1 24.00] CKT 1 | 31.6852 | PASS | 0.41251 | PASS | 312.5126 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 524163 [EAST_PLANT 6 230.00] CKT 1 | 31.7569 | PASS | 0.41224 | PASS | 312.237 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 524163 [EAST_PLANT 6 230.00] CKT 1 | 31.7912 | PASS | 0.41252 | PASS | 312.5165 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 31.8176 | PASS | 0.41221 | PASS | 312.2105 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 31.8451 | PASS | 0.41249 | PASS | 312.4929 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 524010 [ROLLHILLS 6 230.00] CKT 1 | 31.8242 | PASS | 0.41221 | PASS | 312.2128 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 524010 [ROLLHILLS 6 230.00] CKT 1 | 31.8544 | PASS | 0.41249 | PASS | 312.4933 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 523971 [HARRNGTON1 1 24.00] CKT 1 | 31.6626 | PASS | 0.41223 | PASS | 312.2303 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523977 [HARRNG_WST 6 230.00] TO BUS 523971 [HARRNGTON1 1 24.00] CKT 1 | 31.6868 | PASS | 0.41251 | PASS | 312.5128 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523945 [PANTEX_S 3 115.00] TO BUS 523933 [PANTEX_S 1 12.5.00] CKT 2 | 31.8406 | PASS | 0.41221 | PASS | 312.2064 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523945 [PANTEX_S 3 115.00] TO BUS 523933 [PANTEX_S 1 12.5.00] CKT 2 | 31.8677 | PASS | 0.41249 | PASS | 312.4878 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523945 [PANTEX_S 3 115.00] TO BUS 523933 [PANTEX_S 1 12.5.00] CKT 1 | 31.8283 | PASS | 0.41223 | PASS | 312.2325 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523945 [PANTEX_S 3 115.00] TO BUS 523933 [PANTEX_S 1 12.5.00] CKT 1 | 31.8406 | PASS | 0.41221 | PASS | 312.2064 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523945 [PANTEX_S 3 115.00] TO BUS 523933 [PANTEX_S 1 12.5.00] CKT 1 | 31.8658 | PASS | 0.41251 | PASS | 312.5135 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523945 [PANTEX_S 3 115.00] TO BUS 523933 [PANTEX_S 1 12.5.00] CKT 1 | 31.8677 | PASS | 0.41249 | PASS | 312.4878 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523938 [PANTEX_N 3 115.00] TO BUS 523945 [PANTEX_S 3 115.00] CKT 1 | 16.4486 | PASS | 0.42347 | PASS | 323.4668 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523938 [PANTEX_N 3 115.00] TO BUS 523945 [PANTEX_S 3 115.00] CKT 1 | 16.479 | PASS | 0.42336 | PASS | 323.3606 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523931 [HIGHLAND_TP3 115.00] TO BUS 524065 [HIGHLAND 3 115.00] CKT 1 | 31.7513 | PASS | 0.41242 | PASS | 312.4171 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523931 [HIGHLAND_TP3 115.00] TO BUS 524065 [HIGHLAND 3 115.00] CKT 1 | 31.848 | PASS | 0.41255 | PASS | 312.548 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523931 [HIGHLAND_TP3 115.00] TO BUS 524018 [ASARCO_TP 3 115.00] CKT 1 | 52.5123 | PASS | Not Converged | PASS | 0 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523931 [HIGHLAND_TP3 115.00] TO BUS 524018 [ASARCO_TP 3 115.00] CKT 1 | 17.0807 | PASS | 0.42059 | PASS | 320.5894 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523931 [HIGHLAND_TP3 115.00] TO BUS 523945 [PANTEX_S 3 115.00] CKT 1 | 16.523 | PASS | 0.42288 | PASS | 322.8829 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523931 [HIGHLAND_TP3 115.00] TO BUS 523945 [PANTEX_S 3 115.00] CKT 1 | 16.5715 | PASS | 0.42276 | PASS | 322.7614 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523928 [MARTIN 3 115.00] TO BUS 523938 [PANTEX_N 3 115.00] CKT 1 | 16.301 | PASS | 0.42412 | PASS | 324.1211 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523928 [MARTIN 3 115.00] TO BUS 523938 [PANTEX_N 3 115.00] CKT 1 | 16.3322 | PASS | 0.42402 | PASS | 324.0221 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523926 [MAJESTC_WND3 115.00] TO BUS 523948 [MAJESTC-LV21 34.5.00] CKT 1 | 31.7815 | PASS | 0.41262 | PASS | 312.6219 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523926 [MAJESTC_WND3 115.00] TO BUS 523948 [MAJESTC-LV21 34.5.00] CKT 1 | 31.8122 | PASS | 0.41294 | PASS | 312.9402 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523926 [MAJESTC_WND3 115.00] TO BUS 523947 [MAJESTC-LV11 34.5.00] CKT 1 | 31.8389 | PASS | 0.41257 | PASS | 312.5688 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523926 [MAJESTC_WND3 115.00] TO BUS 523947 [MAJESTC-LV11 34.5.00] CKT 1 | 31.868 | PASS | 0.41288 | PASS | 312.8848 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523926 [MAJESTC_WND3 115.00] TO BUS 523928 [MARTIN 3 115.00] CKT 1 | 31.7254 | PASS | 0.41308 | PASS | 313.0784 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523926 [MAJESTC_WND3 115.00] TO BUS 523928 [MARTIN 3 115.00] CKT 1 | 31.7091 | PASS | 0.41341 | PASS | 313.4084 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523924 [CARSON_SUB 3 115.00] TO BUS 523928 [MARTIN 3 115.00] CKT 1 | 30.979 | PASS | 0.41242 | PASS | 312.4204 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523924 [CARSON_SUB 3 115.00] TO BUS 523928 [MARTIN 3 115.00] CKT 1 | 31.0002 | PASS | 0.41272 | PASS | 312.7213 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523924 [CARSON_SUB 3 115.00] TO BUS 523923 [CARSON_SUB 1 13.2.00] CKT 1 | 30.9768 | PASS | 0.41242 | PASS | 312.4201 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523924 [CARSON_SUB 3 115.00] TO BUS 523923 [CARSON_SUB 1 13.2.00] CKT 1 | 30.9976 | PASS | 0.41272 | PASS | 312.7211 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 31.8295 | PASS | 0.41222 | PASS | 312.2214 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 31.8476 | PASS | 0.4125 | PASS | 312.4978 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 31.7871 | PASS | 0.41222 | PASS | 312.2172 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523777 [WHEELER 6 230.00] CKT 1 | 31.8069 | PASS | 0.4125 | PASS | 312.5012 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523770 [GRAPEVINE 3 115.00] CKT 1 | 31.7954 | PASS | 0.41222 | PASS | 312.2171 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523771 [GRAPEVINE 6 230.00] TO BUS 523770 [GRAPEVINE 3 115.00] CKT 1 | 31.8199 | PASS | 0.41249 | PASS | 312.4853 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523712 [KINGSMILL 3 115.00] CKT 2 | 31.8339 | PASS | 0.41221 | PASS | 312.2094 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523712 [KINGSMILL 3 115.00] CKT 2 | 31.8612 | PASS | 0.41249 | PASS | 312.4885 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523712 [KINGSMILL 3 115.00] CKT 1 | 31.835 | PASS | 0.41221 | PASS | 312.2091 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523712 [KINGSMILL 3 115.00] CKT 1 | 31.8624 | PASS | 0.41249 | PASS | 312.4884 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523700 [MCCULUGH_TP2 69.00] CKT 1 | 31.8268 | PASS | 0.41221 | PASS | 312.2087 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523700 [MCCULUGH_TP2 69.00] CKT 1 | 31.8534 | PASS | 0.41249 | PASS | 312.4921 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523512 [SPRINGCREEK2 69.00] CKT 1 | 31.8415 | PASS | 0.41221 | PASS | 312.2063 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523711 [KINGSMILL 2 69.00] TO BUS 523512 [SPRINGCREEK2 69.00] CKT 1 | 31.8711 | PASS | 0.41249 | PASS | 312.4876 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523647 [CRMWA#23TP 2 69.00] TO BUS 523649 [CRMWA#23 2 69.00] CKT 1 | 31.843 | PASS | 0.41221 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523647 [CRMWA#23TP 2 69.00] TO BUS 523649 [CRMWA#23 2 69.00] CKT 1 | 31.8714 | PASS | 0.41249 | PASS | 312.4874 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523647 [CRMWA#23TP 2 69.00] TO BUS 523646 [CRMWA#21 2 69.00] CKT 1 | 31.8459 | PASS | 0.41221 | PASS | 312.2059 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523647 [CRMWA#23TP 2 69.00] TO BUS 523646 [CRMWA#21 2 69.00] CKT 1 | 31.8748 | PASS | 0.41249 | PASS | 312.4871 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523711 [KINGSMILL 2 69.00] CKT 1 | 31.7265 | PASS | 0.41222 | PASS | 312.2224 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523711 [KINGSMILL 2 69.00] CKT 1 | 31.7648 | PASS | 0.41249 | PASS | 312.4911 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523653 [KITE 2 69.00] CKT 1 | 31.8498 | PASS | 0.41221 | PASS | 312.2056 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523653 [KITE 2 69.00] CKT 1 | 31.8715 | PASS | 0.41249 | PASS | 312.4866 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523647 [CRMWA#23TP 2 69.00] CKT 1 | 31.8476 | PASS | 0.41221 | PASS | 312.2061 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523647 [CRMWA#23TP 2 69.00] CKT 1 | 31.8774 | PASS | 0.41249 | PASS | 312.4873 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523636 [GRAY_CNTY 3 115.00] CKT 1 | 31.7279 | PASS | 0.41223 | PASS | 312.231 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523635 [GRAY_CNTY 2 69.00] TO BUS 523636 [GRAY_CNTY 3 115.00] CKT 1 | 31.7707 | PASS | 0.41251 | PASS | 312.5084 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523616 [DAMRON 2 69.00] TO BUS 523635 [GRAY_CNTY 2 69.00] CKT 1 | 31.8442 | PASS | 0.41221 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523616 [DAMRON 2 69.00] TO BUS 523635 [GRAY_CNTY 2 69.00] CKT 1 | 31.8702 | PASS | 0.41249 | PASS | 312.4874 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523616 [DAMRON 2 69.00] TO BUS 523609 [ROXANA 2 69.00] CKT 1 | 31.8422 | PASS | 0.41221 | PASS | 312.2063 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523616 [DAMRON 2 69.00] TO BUS 523609 [ROXANA 2 69.00] CKT 1 | 31.8679 | PASS | 0.41249 | PASS | 312.4875 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523602 [BURNETT 2 69.00] TO BUS 523623 [CRMWA#22 2 69.00] CKT 1 | 31.8435 | PASS | 0.41221 | PASS | 312.2066 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523602 [BURNETT 2 69.00] TO BUS 523623 [CRMWA#22 2 69.00] CKT 1 | 31.8709 | PASS | 0.41249 | PASS | 312.4876 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523551 [HUTCHISON 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 30.5803 | PASS | 0.41253 | PASS | 312.5261 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523551 [HUTCHISON 6 230.00] TO BUS 524044 [NICHOLS 6 230.00] CKT 1 | 30.5913 | PASS | 0.41279 | PASS | 312.7884 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523546 [HUTCH_S 3 115.00] TO BUS 523928 [MARTIN 3 115.00] CKT 1 | 17.4428 | PASS | 0.41845 | PASS | 318.455 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523546 [HUTCH_S 3 115.00] TO BUS 523928 [MARTIN 3 115.00] CKT 1 | 17.4704 | PASS | 0.41929 | PASS | 319.2887 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523546 [HUTCH_S 3 115.00] TO BUS 523636 [GRAY_CNTY 3 115.00] CKT 1 | 31.7281 | PASS | 0.41223 | PASS | 312.2331 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523546 [HUTCH_S 3 115.00] TO BUS 523636 [GRAY_CNTY 3 115.00] CKT 1 | 31.7709 | PASS | 0.41251 | PASS | 312.5102 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523546 [HUTCH_S 3 115.00] TO BUS 523551 [HUTCHISON 6 230.00] CKT 1 | 31.5202 | PASS | 0.4123 | PASS | 312.3022 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523546 [HUTCH_S 3 115.00] TO BUS 523551 [HUTCHISON 6 230.00] CKT 1 | 31.5539 | PASS | 0.41256 | PASS | 312.5635 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523544 [HUTCH_N 3 115.00] TO BUS 523551 [HUTCHISON 6 230.00] CKT 1 | 31.5281 | PASS | 0.4123 | PASS | 312.2998 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523544 [HUTCH_N 3 115.00] TO BUS 523551 [HUTCHISON 6 230.00] CKT 1 | 31.5617 | PASS | 0.41256 | PASS | 312.5612 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523543 [HUTCHISON 2 69.00] TO BUS 523623 [CRMWA#22 2 69.00] CKT 1 | 31.845 | PASS | 0.41221 | PASS | 312.2066 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523543 [HUTCHISON 2 69.00] TO BUS 523623 [CRMWA#22 2 69.00] CKT 1 | 31.8725 | PASS | 0.41249 | PASS | 312.4875 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523543 [HUTCHISON 2 69.00] TO BUS 523546 [HUTCH_S 3 115.00] CKT 1 | 31.663 | PASS | 0.41225 | PASS | 312.2501 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523543 [HUTCHISON 2 69.00] TO BUS 523546 [HUTCH_S 3 115.00] CKT 1 | 31.6982 | PASS | 0.41253 | PASS | 312.5329 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523526 [WEATHERLY 2 69.00] TO BUS 523543 [HUTCHISON 2 69.00] CKT 1 | 31.8451 | PASS | 0.4122 | PASS | 312.1997 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523526 [WEATHERLY 2 69.00] TO BUS 523543 [HUTCHISON 2 69.00] CKT 1 | 31.865 | PASS | 0.41248 | PASS | 312.4847 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523516 [W_BORGER_TP3 115.00] TO BUS 523518 [W_BORGER 3 115.00] CKT 1 | 31.8467 | PASS | 0.41221 | PASS | 312.2097 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523516 [W_BORGER_TP3 115.00] TO BUS 523518 [W_BORGER 3 115.00] CKT 1 | 31.87 | PASS | 0.41249 | PASS | 312.492 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523505 [PHILLPREF2 2 69.00] TO BUS 523526 [WEATHERLY 2 69.00] CKT 1 | 31.8363 | PASS | 0.4122 | PASS | 312.203 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523505 [PHILLPREF2 2 69.00] TO BUS 523526 [WEATHERLY 2 69.00] CKT 1 | 31.8594 | PASS | 0.41249 | PASS | 312.488 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523485 [CAMX/AGR TP3 115.00] TO BUS 523544 [HUTCH_N 3 115.00] CKT 1 | 31.5935 | PASS | 0.4123 | PASS | 312.2962 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523485 [CAMX/AGR TP3 115.00] TO BUS 523544 [HUTCH_N 3 115.00] CKT 1 | 31.635 | PASS | 0.41258 | PASS | 312.5815 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523485 [CAMX/AGR TP3 115.00] TO BUS 523516 [W_BORGER_TP3 115.00] CKT 1 | 31.5946 | PASS | 0.41229 | PASS | 312.2914 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523485 [CAMX/AGR TP3 115.00] TO BUS 523516 [W_BORGER_TP3 115.00] CKT 1 | 31.6332 | PASS | 0.41258 | PASS | 312.5769 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523485 [CAMX/AGR TP3 115.00] TO BUS 523486 [CAMEX/AGRM 3 115.00] CKT 1 | 31.8428 | PASS | 0.41221 | PASS | 312.2094 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523485 [CAMX/AGR TP3 115.00] TO BUS 523486 [CAMEX/AGRM 3 115.00] CKT 1 | 31.8703 | PASS | 0.41249 | PASS | 312.4906 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523484 [CAMEX/TRNSP2 69.00] TO BUS 523543 [HUTCHISON 2 69.00] CKT 1 | 31.7451 | PASS | 0.41222 | PASS | 312.219 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523484 [CAMEX/TRNSP2 69.00] TO BUS 523543 [HUTCHISON 2 69.00] CKT 1 | 31.7762 | PASS | 0.4125 | PASS | 312.5003 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523478 [Q_RYTON_TP 3 115.00] TO BUS 523202 [PHILLIPWRBS3 115.00] CKT 1 | 31.8189 | PASS | 0.41222 | PASS | 312.2162 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523478 [Q_RYTON_TP 3 115.00] TO BUS 523202 [PHILLIPWRBS3 115.00] CKT 1 | 31.8472 | PASS | 0.41249 | PASS | 312.4933 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523445 [BLACKHAWK 2 69.00] TO BUS 523505 [PHILLPREF2 2 69.00] CKT 1 | 31.8308 | PASS | 0.41221 | PASS | 312.2064 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523445 [BLACKHAWK 2 69.00] TO BUS 523505 [PHILLPREF2 2 69.00] CKT 1 | 31.8541 | PASS | 0.41249 | PASS | 312.4873 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523445 [BLACKHAWK 2 69.00] TO BUS 523498 [PHILLPREF1 2 69.00] CKT 1 | 31.8114 | PASS | 0.41222 | PASS | 312.2222 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523445 [BLACKHAWK 2 69.00] TO BUS 523498 [PHILLPREF1 2 69.00] CKT 1 | 31.8294 | PASS | 0.41249 | PASS | 312.4909 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523413 [INDUSTRIAL 2 69.00] TO BUS 523484 [CAMEX/TRNSP2 69.00] CKT 1 | 31.7489 | PASS | 0.41222 | PASS | 312.2167 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523413 [INDUSTRIAL 2 69.00] TO BUS 523484 [CAMEX/TRNSP2 69.00] CKT 1 | 31.7804 | PASS | 0.4125 | PASS | 312.498 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523413 [INDUSTRIAL 2 69.00] TO BUS 523431 [SIDRICHARD 2 69.00] CKT 1 | 31.7013 | PASS | 0.41222 | PASS | 312.2243 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523413 [INDUSTRIAL 2 69.00] TO BUS 523431 [SIDRICHARD 2 69.00] CKT 1 | 31.7394 | PASS | 0.4125 | PASS | 312.502 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523413 [INDUSTRIAL 2 69.00] TO BUS 523421 [HUBER_GEN 2 69.00] CKT 1 | 31.7345 | PASS | 0.41222 | PASS | 312.221 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523413 [INDUSTRIAL 2 69.00] TO BUS 523421 [HUBER_GEN 2 69.00] CKT 1 | 31.7701 | PASS | 0.4125 | PASS | 312.4987 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523405 [CRMWA_#2 3 115.00] TO BUS 523492 [FRITCH 3 115.00] CKT 1 | 31.7815 | PASS | 0.41222 | PASS | 312.2199 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523405 [CRMWA_#2 3 115.00] TO BUS 523492 [FRITCH 3 115.00] CKT 1 | 31.8174 | PASS | 0.4125 | PASS | 312.497 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523404 [CRMWA_#1TP 3 115.00] TO BUS 523405 [CRMWA_#2 3 115.00] CKT 1 | 31.7817 | PASS | 0.41222 | PASS | 312.2199 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523404 [CRMWA_#1TP 3 115.00] TO BUS 523405 [CRMWA_#2 3 115.00] CKT 1 | 31.8178 | PASS | 0.4125 | PASS | 312.4969 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523403 [CRMWA_#1 3 115.00] TO BUS 523404 [CRMWA_#1TP 3 115.00] CKT 1 | 31.8409 | PASS | 0.41221 | PASS | 312.2065 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523403 [CRMWA_#1 3 115.00] TO BUS 523404 [CRMWA_#1TP 3 115.00] CKT 1 | 31.8686 | PASS | 0.41249 | PASS | 312.488 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523377 [RIVERVIEW 3 115.00] TO BUS 523546 [HUTCH_S 3 115.00] CKT 1 | 31.7159 | PASS | 0.41224 | PASS | 312.241 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523377 [RIVERVIEW 3 115.00] TO BUS 523546 [HUTCH_S 3 115.00] CKT 1 | 31.7483 | PASS | 0.41252 | PASS | 312.5247 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523377 [RIVERVIEW 3 115.00] TO BUS 523516 [W_BORGER_TP3 115.00] CKT 1 | 31.5954 | PASS | 0.41229 | PASS | 312.2868 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523377 [RIVERVIEW 3 115.00] TO BUS 523516 [W_BORGER_TP3 115.00] CKT 1 | 31.6358 | PASS | 0.41257 | PASS | 312.5706 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523377 [RIVERVIEW 3 115.00] TO BUS 523404 [CRMWA_#1TP 3 115.00] CKT 1 | 31.7809 | PASS | 0.41222 | PASS | 312.2204 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523377 [RIVERVIEW 3 115.00] TO BUS 523404 [CRMWA_#1TP 3 115.00] CKT 1 | 31.8173 | PASS | 0.4125 | PASS | 312.4971 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523498 [PHILLPREF1 2 69.00] CKT 1 | 31.8597 | PASS | 0.4122 | PASS | 312.1984 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523498 [PHILLPREF1 2 69.00] CKT 1 | 31.8823 | PASS | 0.41248 | PASS | 312.4771 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523413 [INDUSTRIAL 2 69.00] CKT 1 | 31.8293 | PASS | 0.41221 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523413 [INDUSTRIAL 2 69.00] CKT 1 | 31.8585 | PASS | 0.41249 | PASS | 312.4872 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523397 [ROCKYPOINT 2 69.00] CKT 1 | 31.8459 | PASS | 0.41221 | PASS | 312.2065 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523397 [ROCKYPOINT 2 69.00] CKT 1 | 31.8731 | PASS | 0.41249 | PASS | 312.4874 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523377 [RIVERVIEW 3 115.00] CKT 1 | 31.8204 | PASS | 0.4122 | PASS | 312.2024 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523376 [RIVERVIEW 2 69.00] TO BUS 523377 [RIVERVIEW 3 115.00] CKT 1 | 31.8415 | PASS | 0.41249 | PASS | 312.4937 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523367 [RB-SNEED +3 115.00] TO BUS 523366 [RB-SNEED 3 115.00] CKT 1 | 31.8445 | PASS | 0.41221 | PASS | 312.2059 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523367 [RB-SNEED +3 115.00] TO BUS 523366 [RB-SNEED 3 115.00] CKT 1 | 31.8725 | PASS | 0.41249 | PASS | 312.4871 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523367 [RB-SNEED +3 115.00] TO BUS 523304 [MOORE_W 3 115.00] CKT 1 | 31.5606 | PASS | 0.41229 | PASS | 312.2934 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523367 [RB-SNEED +3 115.00] TO BUS 523304 [MOORE_W 3 115.00] CKT 1 | 31.6076 | PASS | 0.41257 | PASS | 312.567 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523352 [HERRING_TP 3 115.00] TO BUS 523377 [RIVERVIEW 3 115.00] CKT 1 | 31.5615 | PASS | 0.4123 | PASS | 312.3001 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523352 [HERRING_TP 3 115.00] TO BUS 523377 [RIVERVIEW 3 115.00] CKT 1 | 31.6101 | PASS | 0.41258 | PASS | 312.5764 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523352 [HERRING_TP 3 115.00] TO BUS 523367 [RB-SNEED +3 115.00] CKT 1 | 31.5611 | PASS | 0.41229 | PASS | 312.2949 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523352 [HERRING_TP 3 115.00] TO BUS 523367 [RB-SNEED +3 115.00] CKT 1 | 31.6088 | PASS | 0.41257 | PASS | 312.5683 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523352 [HERRING_TP 3 115.00] TO BUS 523359 [HERRING 3 115.00] CKT 1 | 31.8484 | PASS | 0.41221 | PASS | 312.2069 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523352 [HERRING_TP 3 115.00] TO BUS 523359 [HERRING 3 115.00] CKT 1 | 31.8743 | PASS | 0.41249 | PASS | 312.488 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523470 [CPCOKER 3 115.00] CKT 1 | 31.8419 | PASS | 0.41221 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523470 [CPCOKER 3 115.00] CKT 1 | 31.869 | PASS | 0.41249 | PASS | 312.4874 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523462 [BLACKHAWK2 1 13.8.00] CKT 1 | 31.4742 | PASS | 0.41226 | PASS | 312.2571 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523462 [BLACKHAWK2 1 13.8.00] CKT 1 | 31.4556 | PASS | 0.41255 | PASS | 312.5476 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523445 [BLACKHAWK 2 69.00] CKT 1 | 31.8309 | PASS | 0.41221 | PASS | 312.2078 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523445 [BLACKHAWK 2 69.00] CKT 1 | 31.8584 | PASS | 0.41249 | PASS | 312.489 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523202 [PHILLIPWRBS3 115.00] CKT 1 | 31.7882 | PASS | 0.41224 | PASS | 312.2428 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523346 [BLKHAWK_E 3 115.00] TO BUS 523202 [PHILLIPWRBS3 115.00] CKT 1 | 31.8209 | PASS | 0.41251 | PASS | 312.505 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523544 [HUTCH_N 3 115.00] CKT 1 | 31.0321 | PASS | 0.4124 | PASS | 312.397 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523544 [HUTCH_N 3 115.00] CKT 1 | 31.0385 | PASS | 0.41271 | PASS | 312.7065 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523470 [CPCOKER 3 115.00] CKT 1 | 31.8422 | PASS | 0.41221 | PASS | 312.2062 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523470 [CPCOKER 3 115.00] CKT 1 | 31.8693 | PASS | 0.41249 | PASS | 312.4874 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523461 [BLACKHAWK1 1 13.8.00] CKT 1 | 31.5197 | PASS | 0.41225 | PASS | 312.2519 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523461 [BLACKHAWK1 1 13.8.00] CKT 1 | 31.4984 | PASS | 0.41254 | PASS | 312.5418 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523445 [BLACKHAWK 2 69.00] CKT 1 | 31.8309 | PASS | 0.41221 | PASS | 312.2077 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523344 [BLKHAWK_W 3 115.00] TO BUS 523445 [BLACKHAWK 2 69.00] CKT 1 | 31.8584 | PASS | 0.41249 | PASS | 312.489 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523267 [PRINGLE 6 230.00] TO BUS 523979 [HARRNG_EST 6 230.00] CKT 1 | 31.7825 | PASS | 0.41221 | PASS | 312.2098 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523267 [PRINGLE 6 230.00] TO BUS 523979 [HARRNG_EST 6 230.00] CKT 1 | 31.8146 | PASS | 0.41249 | PASS | 312.4931 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523478 [Q_RYTON_TP 3 115.00] CKT 1 | 31.824 | PASS | 0.41221 | PASS | 312.2127 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523478 [Q_RYTON_TP 3 115.00] CKT 1 | 31.8515 | PASS | 0.41249 | PASS | 312.4903 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523377 [RIVERVIEW 3 115.00] CKT 1 | 31.5672 | PASS | 0.4123 | PASS | 312.3039 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523377 [RIVERVIEW 3 115.00] CKT 1 | 31.6071 | PASS | 0.41259 | PASS | 312.589 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523267 [PRINGLE 6 230.00] CKT 1 | 31.7809 | PASS | 0.41221 | PASS | 312.2092 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523267 [PRINGLE 6 230.00] CKT 1 | 31.8121 | PASS | 0.41249 | PASS | 312.4934 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523261 [PRINGLE 1 34.5.00] CKT 1 | 31.8432 | PASS | 0.41222 | PASS | 312.2174 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523266 [PRINGLE 3 115.00] TO BUS 523261 [PRINGLE 1 34.5.00] CKT 1 | 31.871 | PASS | 0.4125 | PASS | 312.4981 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523266 [PRINGLE 3 115.00] CKT 2 | 31.8145 | PASS | 0.41222 | PASS | 312.217 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523266 [PRINGLE 3 115.00] CKT 2 | 31.8428 | PASS | 0.4125 | PASS | 312.4986 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523266 [PRINGLE 3 115.00] CKT 1 | 31.7981 | PASS | 0.41223 | PASS | 312.2253 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523266 [PRINGLE 3 115.00] CKT 1 | 31.8275 | PASS | 0.41251 | PASS | 312.5074 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523203 [SPEARMNSUB 3 115.00] CKT 1 | 31.8069 | PASS | 0.41222 | PASS | 312.2181 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523203 [SPEARMNSUB 3 115.00] CKT 1 | 31.836 | PASS | 0.4125 | PASS | 312.4952 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523195 [HANSFORD 3 115.00] CKT 1 | 31.7608 | PASS | 0.41223 | PASS | 312.2347 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523195 [HANSFORD 3 115.00] CKT 1 | 31.7855 | PASS | 0.41251 | PASS | 312.5084 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523185 [SPEARMAN 2 69.00] CKT 1 | 31.839 | PASS | 0.41221 | PASS | 312.2077 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523185 [SPEARMAN 2 69.00] CKT 1 | 31.8692 | PASS | 0.41249 | PASS | 312.4876 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523143 [NP-PERDUR_G3 115.00] CKT 1 | 31.8379 | PASS | 0.41221 | PASS | 312.2111 | 31.82 | 37.56
GEN-2026-PR16 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR16 | 115kV Bus at SPS MARTIN Substation, Carson County, TX | OPEN LINE FROM BUS 523186 [SPEARMAN 3 115.00] TO BUS 523143 [NP-PERDUR_G3 115.00] CKT 1 | 31.8686 | PASS | 0.41249 | PASS | 312.4895 | 31.82 | 37.56

## WSCR
* WSCR is not applicable to this study.