## Executive Summary
Executive Summary: Group 05 GEN-2026-PR18 Priority Process Study
Interconnection Customer GEN-2026-PR18 (Group 05) has requested a Priority System Impact Study pursuant to Section 3.11 of the GIP under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR18 generation for total of:
30 MW
The minimum cost of interconnecting GEN-2026-PR18 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR18 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 9/8/2026
Costs for Thermal Requests were allocated using the 29SP (Summer Peak) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4627300% | SPP | Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR18 | 05 SOUTHWEST | 42 | Priority Process | Thermal | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | SPS | HOBBS_INT 6 230kV | SPECIAL STUDY
GEN-2026-PR17 | 05 SOUTHWEST | 41 | Priority Process | Battery/Storage | 40.5 | [9 empty] | ER | OKGE | Minco 345kV Substation | SPECIAL STUDY
GEN-2026-PR16 | 05 SOUTHWEST | 40 | Priority Process | Wind | 31.82 | [9 empty] | ER | SPS | Martin 115kV | SPECIAL STUDY
GEN-2026-PR15 | 04 SOUTHEAST | 39 | Priority Process | Wind | 31.36 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | SPECIAL STUDY
GEN-2026-PR14 | 04 SOUTHEAST | 38 | Priority Process | Battery/Storage | 43.99 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | SPECIAL STUDY
GEN-2026-PR13 | 04 SOUTHEAST | 37 | Priority Process | Wind | 25.96 | [9 empty] | ER | OG&E | Minco 345kV Substation | SPECIAL STUDY
GEN-2026-PR12 | 04 SOUTHEAST | 36 | Priority Process | Wind | 11.96 | [9 empty] | ER | OG&E | NARDINS2 69kV | SPECIAL STUDY
GEN-2026-PR11 | 05 SOUTHWEST | 35 | Priority Process | Wind | 30 | [9 empty] | ER | SPS | Lost Draw 3 115kV substation | SPECIAL STUDY
GEN-2026-PR9 | 05 SOUTHWEST | 34 | Priority Process | Wind | 15.99 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | SPECIAL STUDY
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | [9 empty] | ER | MIDW | South Hays 230kV | SPECIAL STUDY
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | SPECIAL STUDY
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | SPECIAL STUDY
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | SPECIAL STUDY
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | SPECIAL STUDY
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 30 | 0 | Instability | Multiple Upgrades | 0 | N/A | N/A | 30 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 30 | 0 | Instability | Multiple Upgrades | N/A | 0 | N/A | 30 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 30 | 0 | Instability | Multiple Upgrades | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 30 | 0 | Instability | Multiple Upgrades | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 30 | 0 | Instability | Multiple Upgrades | 0 | N/A | N/A | 30 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 30 | 0 | Instability | Multiple Upgrades | N/A | 0 | N/A | 30 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 30 | 0 | Instability | Multiple Upgrades | N/A | N/A | N/A | 30 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2026-PR18 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 30 | 0 | Instability | Multiple Upgrades | N/A | N/A | N/A | 30 | N/A | N/A | N/A | N/A | N/A | 0

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | 26SP | System Intact | 319 | 319 | 107.71 | 108.28 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | 26SP | System Intact | 319 | 319 | 107.86 | 108.43 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 26SP | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV: | 1125 | 1125 | 126.38 | 127.6 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 26SP | System Intact | 1125 | 1125 | 100.31 | 101.23 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 26SP | 526936 YOAKUM 7 345 787920 G24-365-TAP 345 1 | 497 | 547 | 122.32 | 123.79 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 527362 JOHNSON_DRW3 115 528413 TAYLOR 3 115 1 | 26SP | System Intact | 159 | 175 | 108.75 | 109.61 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 26SP | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV: | 1125 | 1125 | 117.05 | 118.26 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 26SP | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV: | 1125 | 1125 | 120.91 | 122.14 |  |  |  | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
00ALL | GEN-2026-PR18 PSIS | ERIS | Thermal | None | 29SP, 29WP | None | [7 empty] | None
00ALL | GEN-2026-PR18 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00ALL | GEN-2026-PR18 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR18 PSIS | ERIS | Stability | Non-Converged | 298SP, 29WP | Line - Woodward - Crawfish Draw 765 kV New Line Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | [7 empty] | Multiple Upgrades
05ALL | GEN-2026-PR18 PSIS | ERIS | Stability | Angular Instability, Voltage Breakdown | 298SP, 29WP | Multiple Contingencies | [7 empty] | Multiple Upgrades
05ALL | GEN-2026-PR18 PSIS CF | ERIS | Stability | Angular Instability, Voltage Breakdown | 298SP, 29WP | Multiple Contingencies | [7 empty] | Multiple Upgrades
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | [7 empty] | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP | P42:345:SPS:HITCHLAND-1R15:::EHV: | [7 empty] | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | [7 empty] | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Non-Converged | Non-Converged | 26SP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | [7 empty] | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 26SP, 29SP | 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | 773 | 908 | 150.2 | 151.37 |  |  |  | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | 26SP | 515378 WWARD9 765 515375 WWRDEHV7 345 2 | 773 | 908 | 114.71 | 115.35 |  |  |  | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1 | 26SP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 478 | 546 | 128.17 | 130.18 |  |  |  | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 26SP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 1125 | 1125 | 103.14 | 104.13 |  |  |  | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 353 | 353 | 151.63 | 154.13 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 349 | 395 | 142.25 | 144.62 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | 29SP | P42:345:SPS:HITCHLAND-1R15:::EHV: | 498 | 548 | 124.64 | 125.87 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 1098 | 1098 | 117.67 | 119.01 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 29SP | 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | 773 | 908 | 140.66 | 142.14 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 29SP | System Intact | 318.7 | 318.7 | 103.4 | 104.18 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 353 | 353 | 159.6 | 162.25 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 956 | 956 | 106.95 | 108.12 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 956 | 956 | 116.48 | 117.69 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29SP | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | 956 | 956 | 108.56 | 109.74 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 29SP | System Intact | 478 | 610 | 114.77 | 115.29 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2 Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Thermal | 528355 MADDOX 3 115 528392 PEARLE 3 115 1 | 29SP, 29WP | System Intact | 120.1 | 120.1 | 126.9 | 127.63 |  |  |  | Maddox - Pearl 115 kV Ckt 1 Rebuild
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00ALL | GEN-2026-PR18 PSIS CF | ERIS | Non-Converged | None | 29SP, 29WP | None | [7 empty] | None

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.21516 | 4821400% | 883920000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504296 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | 0.08189 | 4821400% | 3304340617.4944
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504237 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward - Potter Co 765 kV Ckt 1 New Line | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 2025 ITP | Yes | N/A | 0.16958 | 4821400% | 1348925000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504184 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03359 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504188 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03359 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504191 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03359 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504177 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 765 kV New Substation | Install 765 kV substation at Anthem | 2025 ITP | Yes | N/A | 0.08189 | 4821400% | 27000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504180 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem 765 kV Reactor | Install 765 kV substation at Anthem | 2025 ITP | Yes | N/A | 0.08189 | 4821400% | 15000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504219 | Line - Crawfish Draw - Phantom 765 kV New Line | Border 345 kV Reactor | Install 100 MVAR reactor at Border 345 kV substation | 2025 ITP | Yes | N/A | 0.03255 | 4821400% | 12000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504210 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw - Phantom 765 kV Ckt 1 New Line | Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom | 2025 ITP | Yes | N/A | 0.16621 | 4821400% | 896306387.8
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 502134 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Crawfish Draw - Phantom 765 kV Ckt 2 New Line | Build a 238.6-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom | 2025 ITP | Yes | N/A | 0.16621 | 4821400% | 896306387.8
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 503551 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 345 kV New Substation | Install 345 kV substation at Crawfish Draw | 2025 ITP | Yes | N/A | 0.23391 | 4821400% | 20441838.66
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500466 | Line - Crawfish Draw - Phantom 765 kV New Line | Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw | Tap the existing Border - Tuco 345 kV Ckt 1 line and extend 4.8 miles to new Crawfish Draw substation | 2025 ITP | Yes | N/A | 0.03255 | 4821400% | 3100000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500461 | Line - Crawfish Draw - Phantom 765 kV New Line | Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw | Tap Oklaunion - Tuco 345 kV and extend 2.88 miles to Crawfish Draw | 2025 ITP | Yes | N/A | 0.08273 | 4821400% | 8928000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504221 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 345 kV Reactor | Install 175 MVAR reactor at Crawfish Draw 345 kV substation | 2025 ITP | Yes | N/A | 0.08273 | 4821400% | 16256703.7325
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504235 | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Crawfish Draw 765 kV Line Reactor | Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation | 2025 ITP | Yes | N/A | 0.23391 | 4821400% | 12271304.934
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504179 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV New Substation | Install 765 kV substation at Crawfish Draw | 2025 ITP | Yes | N/A | 0.23391 | 4821400% | 47284600.47
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | N/A | 0.06112 | 4821400% | 2977710.8841
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500690 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 345 kV New Substation | Install 345 kV substation at Lea National | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 26127351.04
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500691 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 115/345 kV Ckt 1 Transformer | Install new 115/345 kV Ckt 1 transformer at Lea National | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 16908188.08
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500692 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 115 kV Substation Expansion or Rebuild | Expand or rebuild Lea National 115 kV substation | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 24399993.5271
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500693 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 Kv | Lea National 115 kV Ckt 1 Terminal Upgrade toward Lea National 345 kV | Upgrade terminal equipment at Lea National 115 kV substation for Ckt 1 toward Lea National 345 kV | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 851206.91
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500694 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 345 kV Ckt 1 Terminal Upgrade toward Lea National 115 kV | Upgrade terminal equipment at Lea National 345 kV substation for Ckt 1 toward Lea National 115 kV | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 1022599.18
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500695 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 115/345 kV Ckt 2 Transformer | Install new 115/345 kV Ckt 2 transformer at Lea National | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 16908188.08
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500696 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 115 kV Ckt 2 Terminal Upgrade toward Lea National 345 kV | Upgrade terminal equipment at Lea National 115 kV substation for Ckt 2 toward Lea National 345 kV | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 973458.56
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500697 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Lea National 345 kV Ckt 2 Terminal Upgrade toward Lea National 115 kV | Upgrade terminal equipment at Lea National 345 kV substation for Ckt 2 toward Lea National 115 kV | 2025 ITP | Yes | N/A | 0.04215 | 4821400% | 900573.18
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 kV Ckt 2 transformer at Hobbs | 2025 ITP | Yes | N/A | 0.22406 | 4821400% | 16400000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500734 | Multi - Kiowa - Road Runner 345 kV Line Tap at Sand Dunes 115 kV | Kiowa - Road Runner 345 kV Line Tap | Tap the existing Kiowa - Road Runner 345 kV Ckt 1 line at new Sand Dunes substation | 2025 ITP | Yes | N/A | 0.06112 | 4821400% | 4120902
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 502649 | Line - Maddox - Pearl 115 kV Rebuild | Maddox - Pearl 115 kV Ckt 1 Rebuild | Rebuild 15.09-mile Ckt 1 line from Maddox 115 kV substation to Pearl 115 kV substation | 2025 ITP | Yes | N/A | 0.03526 | 4821400% | 15090000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504172 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Crawfish Draw 765 kV Ckt 1 New Line | Build a 284.8-mile 765 kV Ckt 1 line from Minco to Crawfish Draw | 2025 ITP | Yes | N/A | 0.23391 | 4821400% | 1646620000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504167 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Seminole 765 kV Ckt 1 New Line | Build a 99.8-mile 765 kV Ckt 1 line from Minco to Seminole | 2025 ITP | Yes | N/A | 0.154 | 4821400% | 580000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504194 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Minco | 2025 ITP | Yes | N/A | 0.03995 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504198 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Minco | 2025 ITP | Yes | N/A | 0.03995 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504182 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Reactor | Install 150 MVAR reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | 0.03995 | 4821400% | 15000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500764 | North Loving - China Draw 345 kV Line Tap Sendero 345/115 kV New Transformer | North Loving - China Draw 345 kV Line Tap | Tap the existing North Loving - China Draw 345 kV Ckt 1 line at new Sendero substation | 2025 ITP | Yes | N/A | 0.14040 | 4821400% | 5339889.6896
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504217 | Line - Crawfish Draw - Phantom 765 kV New Line | Oklaunion 345 kV Reactor | Install 75 MVAR reactor at Oklaunion 345 kV substation | 2025 ITP | Yes | N/A | -0.05483 | 4821400% | 7500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500770 | Phantom 345/115 kV New Transformer | Phantom 115/345 kV Ckt 4 Transformer | Install new 115/345 kV Ckt 4 transformer at Phantom | 2025 ITP | Yes | N/A | -0.07133 | 4821400% | 19957387.75
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504215 | Line - Crawfish Draw - Phantom 765 kV New Line | Phantom 765 kV Line Reactor | Install 119.6 MVAR line reactor at Phantom 765 kV substation | 2025 ITP | Yes | N/A | 0.16621 | 4821400% | 34195000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500720 | Potash Junction 230/345 kV New Transformer | Potash Junction 230/345 kV Ckt 1 Transformer | Install new 230/345 kV Ckt 1 transformer at Potash Junction | 2025 ITP | Yes | N/A | 0.04126 | 4821400% | 16400000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504247 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Potter Co 765 kV Line Reactor | Install 225 MVAR reactor at Potter Co 765 kV substation | 2025 ITP | Yes | N/A | 0.16958 | 4821400% | 22500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500698 | Road Runner - Whitten - Andrews 345 kV New Line | Road Runner - Whitten 345 kV Ckt 1 New Line | Build a 19-mile 345 kV Ckt 1 line from Road Runner to Whitten | 2025 ITP | Yes | N/A | 0.03162 | 4821400% | 62772073.08
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504171 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Seminole 765 kV Line Reactor | Install 49.9 MVAR line reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.154 | 4821400% | 4990000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504254 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV New Substation | Install 765 kV substation at Seminole | 2025 ITP | Yes | N/A | 0.154 | 4821400% | 27000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504257 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Reactor | Install 150 MVAR reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.154 | 4821400% | 15000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504248 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.6-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | -0.07632 | 4821400% | 1822360000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504259 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Southwest Shreveport | 2025 ITP | Yes | N/A | -0.03816 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504263 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Southwest Shreveport | 2025 ITP | Yes | N/A | -0.03816 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504251 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Line Reactor | Install 157.3 MVAR line reactor at Southwest Shreveport 765 kV substation toward Seminole 765 kV | 2025 ITP | Yes | N/A | -0.07632 | 4821400% | 15730000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504253 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV New Substation | Install 765 kV substation at Southwest Shreveport | 2025 ITP | Yes | N/A | -0.07632 | 4821400% | 27000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504255 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Reactor | Install 150 MVAR reactor at Southwest Shreveport 765 kV substation | 2025 ITP | Yes | N/A | -0.07632 | 4821400% | 15000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504304 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Viola | 2025 ITP | Yes | N/A | 0.04442 | 4821400% | 104567202
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504308 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Viola | 2025 ITP | Yes | N/A | 0.04442 | 4821400% | 104567202
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504311 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Viola | 2025 ITP | Yes | N/A | 0.04442 | 4821400% | 104567202
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504301 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV New Substation | Install 765 kV substation at Viola | 2025 ITP | Yes | N/A | 0.21516 | 4821400% | 107081651
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504302 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Reactor | Install 150 MVAR reactor at Viola 765 kV substation | 2025 ITP | Yes | N/A | 0.21516 | 4821400% | 266653225
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500702 | Road Runner - Whitten - Andrews 345 kV New Line | Whitten - Andrews 345 kV Ckt 1 New Line | Build a 22.6-mile 345 kV Ckt 1 line from Whitten to Andrews | 2025 ITP | Yes | N/A | 0.03919 | 4821400% | 74665729.032
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 500706 | Road Runner - Whitten - Andrews 345 kV New Line | Whitten 345 kV New Substation | Install 345 kV substation at Whitten | 2025 ITP | Yes | N/A | 0.03919 | 4821400% | 7998452.87
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504279 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward - Crawfish Draw 765 kV Ckt 1 New Line | Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw | 2025 ITP | Yes | N/A | 0.14002 | 4821400% | 1528880000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504245 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | 0.21516 | 4821400% | 13000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504285 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Woodward | 2025 ITP | Yes | N/A | 0.04722 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504288 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Woodward | 2025 ITP | Yes | N/A | 0.04722 | 4821400% | 61500000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504284 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV New Substation | Install 765 kV substation at Woodward | 2025 ITP | Yes | N/A | 0.04722 | 4821400% | 27000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | 504243 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.21516 | 4821400% | 30000000
GEN-2026-PR18 | 05 SOUTHWEST | ER | 210628 | 122823 | Border - Woodward Tap 345 kV Substation | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | N/A | 0.03255 | TBD | 23239179
GEN-2026-PR18 | 05 SOUTHWEST | ER | 210627 | 143182 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | N/A | 0.06186 | TBD | 12238460
GEN-2026-PR18 | 05 SOUTHWEST | ER | 210670 | 133085 | Minco - Pleasant Valley 345 kV Ckt 1 | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | N/A | 0.04394 | TBD | 38537430
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | TBD | Potter to Tolk 345 kV Double Circuit Line Build | Potter to Tolk 345 kV Double Circuit Line Build | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | DISIS-2018-002/2019-001 | Yes | N/A | 0.05397 | TBD | 315122604
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | DISIS-2020-001 | Yes | N/A | 0.03843 | TBD | 73524573
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | N/A | 0.03791 | TBD | 428620878
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | N/A | 0.03255 | TBD | 35352000
GEN-2026-PR18 | 05 SOUTHWEST | ER | TBD | TBD | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | N/A | 0.03526 | TBD | TBD

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | 500461, 500466, 504210, 504211, 504212, 504213, 504214, 504215, 504216, 504179, 504217, 504218, 504219, 504220, 504221, 504223, 504225, 504226, 504227, 504228, 504229, 504230, 504231, 504232, 504233, 504234 | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line | Contingent | Tap Oklaunion - Tuco 345 kV and extend 2.88 miles to Crawfish Draw Tap the existing Border - Tuco 345 kV Ckt 1 line and extend 4.8 miles to new Crawfish Draw substation Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Expand or rebuild Phantom 765 kV substation Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 1 toward Phantom 765 kV Upgrade terminal equipment at Phantom 765 kV substation for Ckt 1 toward Crawfish Draw 765 kV Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation toward Phantom 765 kV Install 119.6 MVAR line reactor at Phantom 765 kV substation toward Crawfish Draw 765 kV Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Expand or rebuild Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Expand or rebuild Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 kV Ckt 1 transformer at Crawfish Draw Upgrade terminal equipment at Crawfish Draw 345 kV substation for Ckt 1 toward Crawfish Draw 765 kV Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 1 toward Crawfish Draw 345 kV Install new 345/765 kV Ckt 2 transformer at Crawfish Draw Upgrade terminal equipment at Crawfish Draw 345 kV substation for Ckt 2 toward Crawfish Draw 765 kV Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 2 toward Crawfish Draw 345 kV Install new 345/765 kV Ckt 3 transformer at Crawfish Draw Upgrade terminal equipment at Crawfish Draw 345 kV substation for Ckt 3 toward Crawfish Draw 765 kV Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 3 toward Crawfish Draw 345 kV | 0 | 0% | 928776226.46 | 0.23975
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | 502134, 504211, 502135, 502136, 504235, 504236 | ERIS | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | Contingent | Build a 238.6-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom Expand or rebuild Phantom 765 kV substation Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 2 toward Phantom 765 kV Upgrade terminal equipment at Phantom 765 kV substation for Ckt 2 toward Crawfish Draw 765 kV Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Install 119.6 MVAR line reactor at Phantom 765 kV substation | 0 | 0% | 968765506.734 | 0.23975
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | 170051, 170054, 170078, 170079, 170080, 170091, 170558, 170561, 170068, 170560, 170563, 170096, 170559, 170562 | ERIS | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV | Contingent | Build a new 123.7 mile 765 kV Ckt 1 line from Tecovas 765 kV substation to Crossroads 765 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Bandit substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. Install at least -150 MVAR reactor at Crossroads 765 kV substation looking to Phantom 765 kV substation Install new 765/345 transformer at Crossroads 345 kV substation Install 765 kV Substation at Crossroads and install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation with a summer emergency rating of 5300 MVA and any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter County 765 kV substation with a summer emergency rating of 5300 MVA. Install 765 kV Substation at Bandit and install any necessary terminal equipment at Bandit 765 kV substation to support a new line from Bandit 765 kV substation to Crossroads 765 kV substation with a summer emergency rating of 5300 MVA. Install 765 kV Substation at Tecovas and install any necessary terminal equipment at Tecovas 765 kV substation to support a new line from Tecovas 765 kV substation to Crossroads 765 kV substation with a summer emergency rating of 5300 MVA. Install new 765/345 transformer at Bandit 345 kV substation Install new 765/345 transformer at Tecovas 345 kV substation Install new 765/345 transformer at Bandit 345 kV substation Install new 765/345 transformer at Tecovas 345 kV substation Install new 765/345 transformer at Crossroads 345 kV substation Install new 765/345 transformer at Bandit 345 kV substation Install new 765/345 transformer at Tecovas 345 kV substation Install new 765/345 transformer at Crossroads 345 kV substation Install at least -150 MVAR reactor at Crossroads 765 kV line to Potter County Install at least -150 MVAR reactor at Tecovas looking toward Crossroads Install at least -150 MVAR reactor at Bandit looking toward Crossroads Expand Crossroads 345 kV substation Expand Phantom 345 kV substation Expand Potter County 345 kV substation Build Bandit 345 kV substation Build Tecovas 345 kV substation Build a new 345 kV Ckt 1 line from Tecovas 345 kV substation to Potter County 345 kV substation. Build a new 345 kV Ckt 2 line from Tecovas 345 kV substation to Potter County 345 kV substation. Build a new 345 kV Ckt 3 line from Tecovas 345 kV substation to Potter County 345 kV substation. Build a new 345 kV Ckt 1 line from Bandit 345 kV substation to Phantom 345 kV substation. Build a new 345 kV Ckt 2 line from Bandit 345 kV substation to Phantom 345 kV substation. Build a new 345 kV Ckt 3 line from Bandit 345 kV substation to Phantom 345 kV substation. | 0 | 0% | 4611600652.02 | 0.23975
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | 504237, 504285, 504284 | ERIS | Woodward - Potter Co 765 kV Ckt 1 New Line | Contingent | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co Install new 345/765 Ckt 1 transformer at Woodward Install 765 kV substation at Woodward | 0 | 0% | 1289100000 | 0.23975
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | TBD | ERIS | Hobbs_Int 6 230kV Substation GEN-2026-PR18 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR18 (30/Thermal), into Hobbs_Int 6 230kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | TBD | ERIS | Hobbs_Int 6 230kV Substation GEN-2026-PR18 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR18 (30/Thermal), into Hobbs_Int 6 230kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | 504291,504292,504293,504294,504295,504296,504297,504298,504299,504300,504301,504180,504181,504302,504303,504304,504305,504306,504307,504308,504309,504310,504311,504312,504313 | ERIS | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Contingent | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Woodward 765 kV Install 70.4 MVAR line reactor at Woodward 765 kV substation Install 70.4 MVAR line reactor at Viola 765 kV substation Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola Upgrade terminal equipment at Anthem 765 kV substation for Ckt 1 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Anthem 765 kV Install 83 MVAR line reactor at Anthem 765 kV substation Install 83 MVAR line reactor at Viola 765 kV substation Install 765 kV substation at Viola Install 150 MVAR reactor at Anthem 765 kV substation Expand or rebuild Anthem 765 kV substation Install 150 MVAR reactor at Viola 765 kV substation Expand or rebuild Viola 765 kV substation Install new 345/765 kV Ckt 1 transformer at Viola Expand or rebuild Viola 345 kV substation Upgrade terminal equipment at Viola 345 kV substation for Ckt 1 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Viola 345 kV Install new 345/765 kV Ckt 2 transformer at Viola Upgrade terminal equipment at Viola 345 kV substation for Ckt 2 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 2 toward Viola 345 kV Install new 345/765 kV Ckt 3 transformer at Viola Upgrade terminal equipment at Viola 345 kV substation for Ckt 3 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 3 toward Viola 345 kV | 0 | 0% | 3304340617.4944 | 0.23975
GEN-2026-PR18 | GEN-2026-PR18 PSIS | 05 SOUTHWEST | 504237, 504238, 504239, 504240, 504241, 504242, 504243, 504244, 504245, 504246, 504247 | ERIS | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Contingent | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co Expand or rebuild Potter Co 765 kV substation Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Potter Co 765 kV Upgrade terminal equipment at Potter Co 765 kV substation for Ckt 1 toward Woodward 765 kV Install 104 MVAR line reactor at Woodward 765 kV substation Install 104 MVAR line reactor at Potter Co 765 kV substation Install 375 MVAR reactor at Woodward 765 kV substation Expand or rebuild Woodward 765 kV substation Install 225 MVAR reactor at Woodward 345 kV substation Expand or rebuild Woodward 345 kV substation Install 225 MVAR reactor at Potter Co 765 kV substation | 0 | 0% | 1348925000 | 0.23975
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | 500461, 500466, 504210, 504211, 504212, 504213, 504214, 504215, 504216, 504179, 504217, 504218, 504219, 504220, 504221, 504223, 504225, 504226, 504227, 504228, 504229, 504230, 504231, 504232, 504233, 504234 | ERIS | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Contingent | Expand or rebuild Lea National 115 kV substation Install 345 kV substation at Lea National Install new 115/345 kV Ckt 1 transformer at Lea National Install new 115/345 kV Ckt 2 transformer at Lea National Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation Upgrade terminal equipment at Lea National 115 kV substation for Ckt 1 toward Lea National 345 kV Upgrade terminal equipment at Lea National 115 kV substation for Ckt 2 toward Lea National 345 kV Upgrade terminal equipment at Lea National 345 kV substation for Ckt 1 toward Lea National 115 kV Upgrade terminal equipment at Lea National 345 kV substation for Ckt 2 toward Lea National 115 kV | 0 | 0% | 91069269.4413 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% |  | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | 504321, 504322, 504323, 504324, 504325 | ERIS | XFR - Hobbs 230/115 kV | Contingent | Install new 230/345 Ckt 2 transformer at Hobbs | 0 | 0% | 18874145 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | 122823 | ERIS | Border - Woodward Tap 345 kV Substation | Contingent | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 0 | 0% | 23239179 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 0 | 0% | 12238460 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 | Contingent | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 with a minimum rating of 312 MVA | 0 | 0% | 21900000 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Contingent | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 0 | 0% | 315122604 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | 0 | 0% | 428620878 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Maddox - Pearl 115 kV Ckt 1 Rebuild | Contingent | Build a new MADDOX 3 to PEARLE 3 115 kV line 1 (15.33 miles) to a standard rating of 5300 MVA | 0 | 0% | 15090000 | N/A
GEN-2026-PR18 | GEN-2026-PR18 PSIS CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a new BECKHAM7 to POTTER_CO 7 345 kV line 2 (149.64 miles) to a standard rating of 1792 MVA | 0 | 0% | 222551930 | N/A
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR18 PSIS | Steady State\Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line | 500461, 500466, 504210, 504211, 504212, 504213, 504214, 504215, 504216, 504179, 504217, 504218, 504219, 504220, 504221, 504223, 504225, 504226, 504227, 504228, 504229, 504230, 504231, 504232, 504233, 504234 | Tap Oklaunion - Tuco 345 kV and extend 2.88 miles to Crawfish Draw Tap the existing Border - Tuco 345 kV Ckt 1 line and extend 4.8 miles to new Crawfish Draw substation Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Expand or rebuild Phantom 765 kV substation Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 1 toward Phantom 765 kV Upgrade terminal equipment at Phantom 765 kV substation for Ckt 1 toward Crawfish Draw 765 kV Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation toward Phantom 765 kV Install 119.6 MVAR line reactor at Phantom 765 kV substation toward Crawfish Draw 765 kV Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Expand or rebuild Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Expand or rebuild Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 kV Ckt 1 transformer at Crawfish Draw Upgrade terminal equipment at Crawfish Draw 345 kV substation for Ckt 1 toward Crawfish Draw 765 kV Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 1 toward Crawfish Draw 345 kV Install new 345/765 kV Ckt 2 transformer at Crawfish Draw Upgrade terminal equipment at Crawfish Draw 345 kV substation for Ckt 2 toward Crawfish Draw 765 kV Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 2 toward Crawfish Draw 345 kV Install new 345/765 kV Ckt 3 transformer at Crawfish Draw Upgrade terminal equipment at Crawfish Draw 345 kV substation for Ckt 3 toward Crawfish Draw 765 kV Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 3 toward Crawfish Draw 345 kV | SPS | 4821400% | 928776226.46
Contingent | GEN-2026-PR18 PSIS | Steady State\Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Crawfish Draw - Phantom 765 kV New Ckt 2 Line | 502134, 504211, 502135, 502136, 504235, 504236 | Build a 238.6-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom Expand or rebuild Phantom 765 kV substation Upgrade terminal equipment at Crawfish Draw 765 kV substation for Ckt 2 toward Phantom 765 kV Upgrade terminal equipment at Phantom 765 kV substation for Ckt 2 toward Crawfish Draw 765 kV Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Install 119.6 MVAR line reactor at Phantom 765 kV substation | SPS | 4821400% | 968765506.734
Contingent | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV | 170051, 170054, 170078, 170079, 170080, 170091, 170558, 170561, 170068, 170560, 170563, 170096, 170559, 170562 | Build a new 123.7 mile 765 kV Ckt 1 line from Tecovas 765 kV substation to Crossroads 765 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Bandit substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. Install at least -150 MVAR reactor at Crossroads 765 kV substation looking to Phantom 765 kV substation Install new 765/345 transformer at Crossroads 345 kV substation Install 765 kV Substation at Crossroads and install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation with a summer emergency rating of 5300 MVA and any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter County 765 kV substation with a summer emergency rating of 5300 MVA. Install 765 kV Substation at Bandit and install any necessary terminal equipment at Bandit 765 kV substation to support a new line from Bandit 765 kV substation to Crossroads 765 kV substation with a summer emergency rating of 5300 MVA. Install 765 kV Substation at Tecovas and install any necessary terminal equipment at Tecovas 765 kV substation to support a new line from Tecovas 765 kV substation to Crossroads 765 kV substation with a summer emergency rating of 5300 MVA. Install new 765/345 transformer at Bandit 345 kV substation Install new 765/345 transformer at Tecovas 345 kV substation Install new 765/345 transformer at Bandit 345 kV substation Install new 765/345 transformer at Tecovas 345 kV substation Install new 765/345 transformer at Crossroads 345 kV substation Install new 765/345 transformer at Bandit 345 kV substation Install new 765/345 transformer at Tecovas 345 kV substation Install new 765/345 transformer at Crossroads 345 kV substation Install at least -150 MVAR reactor at Crossroads 765 kV line to Potter County Install at least -150 MVAR reactor at Tecovas looking toward Crossroads Install at least -150 MVAR reactor at Bandit looking toward Crossroads Expand Crossroads 345 kV substation Expand Phantom 345 kV substation Expand Potter County 345 kV substation Build Bandit 345 kV substation Build Tecovas 345 kV substation Build a new 345 kV Ckt 1 line from Tecovas 345 kV substation to Potter County 345 kV substation. Build a new 345 kV Ckt 2 line from Tecovas 345 kV substation to Potter County 345 kV substation. Build a new 345 kV Ckt 3 line from Tecovas 345 kV substation to Potter County 345 kV substation. Build a new 345 kV Ckt 1 line from Bandit 345 kV substation to Phantom 345 kV substation. Build a new 345 kV Ckt 2 line from Bandit 345 kV substation to Phantom 345 kV substation. Build a new 345 kV Ckt 3 line from Bandit 345 kV substation to Phantom 345 kV substation. | SPS | 4798300% | 4611600652.02
Contingent | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Potter Co 765 kV Ckt 1 New Line | 504237, 504285, 504284 | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co Install new 345/765 Ckt 1 transformer at Woodward Install 765 kV substation at Woodward | SPS/OKGE | 4821400% | 1289100000
Contingent | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | TBD | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | OKGE | TBD | 428620878
Contingent | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | 2020 ITP | ERIS | Border - Woodward Tap 345 kV Substation | 122823 | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | OKGE | 4586900% | 23239179
Contingent | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEP | 4600200% | 12238460
Contingent | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | 2020 ITP | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 | TBD | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 with a minimum rating of 312 MVA | SPS | TBD | 21900000
Contingent | GEN-2026-PR18 PSIS | Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | 504291,504292,504293,504294,504295,504296,504297,504298,504299,504300,504301,504180,504181,504302,504303,504304,504305,504306,504307,504308,504309,504310,504311,504312,504313 | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Woodward 765 kV Install 70.4 MVAR line reactor at Woodward 765 kV substation Install 70.4 MVAR line reactor at Viola 765 kV substation Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola Upgrade terminal equipment at Anthem 765 kV substation for Ckt 1 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Anthem 765 kV Install 83 MVAR line reactor at Anthem 765 kV substation Install 83 MVAR line reactor at Viola 765 kV substation Install 765 kV substation at Viola Install 150 MVAR reactor at Anthem 765 kV substation Expand or rebuild Anthem 765 kV substation Install 150 MVAR reactor at Viola 765 kV substation Expand or rebuild Viola 765 kV substation Install new 345/765 kV Ckt 1 transformer at Viola Expand or rebuild Viola 345 kV substation Upgrade terminal equipment at Viola 345 kV substation for Ckt 1 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 1 toward Viola 345 kV Install new 345/765 kV Ckt 2 transformer at Viola Upgrade terminal equipment at Viola 345 kV substation for Ckt 2 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 2 toward Viola 345 kV Install new 345/765 kV Ckt 3 transformer at Viola Upgrade terminal equipment at Viola 345 kV substation for Ckt 3 toward Viola 765 kV Upgrade terminal equipment at Viola 765 kV substation for Ckt 3 toward Viola 345 kV | AEP/EKC/OKGE | 4821400% | 3304340617.4944
Contingent | GEN-2026-PR18 PSIS | Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | 504237, 504238, 504239, 504240, 504241, 504242, 504243, 504244, 504245, 504246, 504247 | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co Expand or rebuild Potter Co 765 kV substation Upgrade terminal equipment at Woodward 765 kV substation for Ckt 1 toward Potter Co 765 kV Upgrade terminal equipment at Potter Co 765 kV substation for Ckt 1 toward Woodward 765 kV Install 104 MVAR line reactor at Woodward 765 kV substation Install 104 MVAR line reactor at Potter Co 765 kV substation Install 375 MVAR reactor at Woodward 765 kV substation Expand or rebuild Woodward 765 kV substation Install 225 MVAR reactor at Woodward 345 kV substation Expand or rebuild Woodward 345 kV substation Install 225 MVAR reactor at Potter Co 765 kV substation | OKGE/SPS | 4821400% | 1348925000
Contingent | GEN-2026-PR18 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Maddox - Pearl 115 kV Ckt 1 Rebuild | TBD | Build a new MADDOX 3 to PEARLE 3 115 kV line 1 (15.33 miles) to a standard rating of 5300 MVA | SPS | 4821400% | 15090000
Contingent | GEN-2026-PR18 PSIS CF | Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | 500461, 500466, 504210, 504211, 504212, 504213, 504214, 504215, 504216, 504179, 504217, 504218, 504219, 504220, 504221, 504223, 504225, 504226, 504227, 504228, 504229, 504230, 504231, 504232, 504233, 504234 | Expand or rebuild Lea National 115 kV substation Install 345 kV substation at Lea National Install new 115/345 kV Ckt 1 transformer at Lea National Install new 115/345 kV Ckt 2 transformer at Lea National Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation Upgrade terminal equipment at Lea National 115 kV substation for Ckt 1 toward Lea National 345 kV Upgrade terminal equipment at Lea National 115 kV substation for Ckt 2 toward Lea National 345 kV Upgrade terminal equipment at Lea National 345 kV substation for Ckt 1 toward Lea National 115 kV Upgrade terminal equipment at Lea National 345 kV substation for Ckt 2 toward Lea National 115 kV | SPS | 4725600% | 91069269.4413
Contingent | GEN-2026-PR18 PSIS CF | Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Andrews to Road Runner 345 kV Line | 170597 | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | SPS | 36 | 73524573
Contingent | GEN-2026-PR18 PSIS CF | Stability | 05 SOUTHWEST | 2025 ITP | ERIS | XFR - Hobbs 230/115 kV | 504321, 504322, 504323, 504324, 504325 | Install new 230/345 Ckt 2 transformer at Hobbs | SPS | 4689100% | 18874145
Contingent | GEN-2026-PR18 PSIS CF | Stability | 05 SOUTHWEST | DISIS-2018-002/2019-001 | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | TBD | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | SPS | 36 | 315122604
Contingent | GEN-2026-PR18 PSIS CF | Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | TBD | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | SPS | 36 | 428620878
Interconnection | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR18 PSIS | ERIS | Hobbs_Int 6 230kV Substation GEN-2026-PR18 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR18 (30/Thermal), into Hobbs_Int 6 230kV Substation | SPS | TBD | TBD
Interconnection | GEN-2026-PR18 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR18 PSIS | ERIS | Hobbs_Int 6 230kV Substation GEN-2026-PR18 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR18 (30/Thermal), into Hobbs_Int 6 230kV Substation | SPS | TBD | TBD
13879807989.1496

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR18 | 05 SOUTHWEST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00149 | -0.0447 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.0033 | -0.099 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | 0.00081 | 0.0243 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | 0.00081 | 0.0243 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -1e-05 | -0.0003 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00453 | 0.1359 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.00184 | 0.0552 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -4e-05 | -0.0012 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -4e-05 | -0.0012 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00035 | 0.0105 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00034 | 0.0102 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00149 | 0.0447 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00042 | 0.0126 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | 0.00033 | 0.0099 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00033 | -0.0099 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00525 | -0.1575 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.0027 | -0.081 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 6e-05 | 0.0018 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | -6e-05 | -0.0018 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00011 | 0.0033 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00014 | 0.0042 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00014 | 0.0042 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00015 | 0.0045 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 0 | 0 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 0 | 0 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 0 | 0 | No
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 0 | 0 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR18 | 05 SOUTHWEST | G00 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.40728 | 127.6 | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.40728 | 127.5 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.40728 | 127.46 | P42:345:SPS:TUCO-NR50:::EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.39607 | 124.61 | 526936 YOAKUM 7 345 787920 G24-365-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.25375 | 123.79 | 526936 YOAKUM 7 345 787920 G24-365-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.39662 | 122.2 | P12:345:SPS:J18:1:YOAKUM34_HOBBSINT___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.40883 | 122.14 | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.40883 | 122.04 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.40883 | 122 | P42:345:SPS:TUCO-NR50:::EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.22607 | 120.95 | P12:345:SPS:J15:1:TOLK_CROSSROADS___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.22607 | 120.95 | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.2543 | 119.79 | P12:345:SPS:J18:1:YOAKUM34_HOBBSINT___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.39762 | 119.24 | 526936 YOAKUM 7 345 787920 G24-365-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.4098 | 118.26 | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.4098 | 118.16 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.4098 | 118.12 | P42:345:SPS:TUCO-NR50:::EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.22638 | 118.13 | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33424 | 116.65 | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33424 | 116.65 | P12:230:SPS:K65:1:OASIS_SNJUANTAP___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.39817 | 116.81 | P12:345:SPS:J18:1:YOAKUM34_HOBBSINT___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.22658 | 116.48 | P42:345:SPS:CROSSROADS_6R45:::EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 497 | 547 | 0.22658 | 116.41 | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.39858 | 115.47 | 526936 YOAKUM 7 345 787920 G24-365-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.39913 | 113.07 | P12:345:SPS:J18:1:YOAKUM34_HOBBSINT___:EHV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33578 | 111.25 | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33578 | 111.25 | P12:230:SPS:K65:1:OASIS_SNJUANTAP___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 527362 JOHNSON_DRW3 115 528413 TAYLOR 3 115 1 | 159 | 175 | 0.04295 | 109.61 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33628 | 109.6 | P12:230:SPS:K66:1:SNJUANTAP_CHAVESCNTY___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.32975 | 109.43 | P12:230:SPS:K33:1:AMOCOSS_YOAKUM___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | 319 | 319 | 0.05201 | 108.43 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | 319 | 319 | 0.05201 | 108.28 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.33675 | 107.55 | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.33675 | 107.54 | P12:230:SPS:K65:1:OASIS_SNJUANTAP___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33456 | 107.46 | P12:230:SPS:R07:1:YOAKUM_INKBASIN___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.32975 | 106.67 | P12:230:SPS:K03:1:SUNDOWN_AMOCOSS___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.3135 | 106.42 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.34288 | 105.77 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.3067 | 104.78 | P12:115:SPS:U06.1.RDRN.AGREDHLL:::HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.331 | 104.43 | 526935 YOAKUM 6 230 777420 G24-015-TAP 230 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.29007 | 104.05 | 527896 HOBBS_INT 7 345 780690 G24-124-TAP 345 2 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.30671 | 104.06 | P13:069-115:SPS:1:EAGLE:CREEKTR2___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.30724 | 104.01 | P12:115:SPS:U78.1.ACRNCH.TAYLOR:::HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33783 | 104.11 | P12:230:SPS:K66:1:SNJUANTAP_CHAVESCNTY___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.3313 | 103.92 | P12:230:SPS:K33:1:AMOCOSS_YOAKUM___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.29016 | 103.76 | 527896 HOBBS_INT 7 345 779160 G24-073-TAP 345 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.31174 | 103.64 | 515378 WWARD9 765 526001 CRDRW9 765 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33611 | 101.94 | P12:230:SPS:R07:1:YOAKUM_INKBASIN___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.3067 | 101.23 | System Intact | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.3313 | 101.13 | P12:230:SPS:K03:1:SUNDOWN_AMOCOSS___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.31505 | 100.89 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.3388 | 100.43 | P12:230:SPS:K66:1:SNJUANTAP_CHAVESCNTY___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 527656 CROSSROAD 345 778260 G24-043-TAP 345 1 | 1125 | 1125 | 0.33227 | 100.24 | P12:230:SPS:K33:1:AMOCOSS_YOAKUM___:HV: | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 778260 G24-043-TAP 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.34443 | 100.22 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Line - Potter County 765 kV - Crossroads 765 kV - Phantom 765 kV Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Potter Co 765 kV Ckt 1 New Line
Non-Converged | GEN-2026-PR18 PSIS | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR18 PSIS | 05ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR18 PSIS | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR18 PSIS | 05ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 528355 MADDOX 3 115 528392 PEARLE 3 115 1 | 120.1 | 120.1 | 0.03211 | 127.63 | System Intact | TDF Impact | Maddox - Pearl 115 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.22682 | 162.25 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.22678 | 154.13 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.22682 | 144.62 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21159 | 140.87 | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21159 | 140.83 | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.21156 | 133.63 | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.21156 | 133.6 | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | 498 | 548 | 0.20964 | 125.87 | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | 498 | 548 | 0.20964 | 125.87 | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.21159 | 125.5 | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.21159 | 125.47 | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.34395 | 119.01 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956 | 956 | 0.28263 | 117.69 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21348 | 114.12 | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 956 | 956 | 0.28266 | 109.74 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.21344 | 109.56 | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 956 | 956 | 0.28266 | 108.12 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 318.7 | 318.7 | 0.07948 | 104.18 | System Intact | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.21348 | 101.62 | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39043 | 142.14 | 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.33355 | 138 | System Intact | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.37939 | 136.74 | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.54 | 515458 BORDER 7 345 525839 G17-151TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.47 | 511584 O.K.U.2-7 345 525839 G17-151TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.46 | 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.46 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.33 | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.33 | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.32 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 133.32 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 132.52 | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39211 | 132.52 | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.393 | 132.36 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39301 | 131.78 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39301 | 131.77 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39301 | 131.77 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39312 | 128.29 | 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.39314 | 128.17 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.36777 | 127.24 | P12:230:SPS:K73:1:GRAPEVINE_WHEELER___:HV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.34063 | 127.22 | P42:345:OKGE:SB_MICO7312:::EHV: | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Border to Beckham 345 kV New Line
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06681 | 115.29 | System Intact | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2 Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29WP | GEN-2026-PR18 | FROM->TO | 528355 MADDOX 3 115 528392 PEARLE 3 115 1 | 120.1 | 120.1 | 0.03241 | 126.21 | System Intact | TDF Impact | Maddox - Pearl 115 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.34108 | 151.37 | 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.34108 | 150.69 | 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1 | 478 | 546 | 0.20906 | 130.18 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.35074 | 115.35 | 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR18 | TO->FROM | 525549 TOLK 7 345 780240 G24-109-TAP 345 1 | 1125 | 1125 | 0.33151 | 104.13 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Crawfish Draw 345 kV New Substation Build New Beckham to Potter 345 kV Line Ckt 2 Border - Woodward Tap 345 kV Substation Oklaunion - Tuco 345 kV Line Tap and Extension to Crawfish Draw Border - Tuco 345 kV Line Tap and Extension to Crawfish Draw
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR18 | FROM->TO | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.35074 | 104.79 | 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Build New Beckham to Potter 345 kV Line Ckt 2
Thermal | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR18 | TO->FROM | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 773 | 908 | 0.2948 | 100.25 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line
Non-Converged | GEN-2026-PR18 PSIS CF | 05ALL | 0 | 26SP | N/A | " | Non-Converged | 0 | 0 | N/A | 0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
Non-Converged | GEN-2026-PR18 PSIS CF | 05ALL | 0 | 26SP | N/A | " | Non-Converged | 0 | 0 | N/A | 0 | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
Non-Converged | GEN-2026-PR18 PSIS CF | 05ALL | 0 | 26SP | N/A | " | Non-Converged | 0 | 0 | N/A | 0 | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | TDF Impact | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
Non-Converged | GEN-2026-PR18 PSIS CF | 05ALL | 1 | 26SP | N/A | " | Non-Converged | 0 | 0 | N/A | 0 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Woodward - Potter Co 765 kV Ckt 1 New Line Woodward 345/765 kV Ckt 1 Transformer Woodward 765 kV New Substation
Non-Converged | GEN-2026-PR18 PSIS CF | 05ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR18 PSIS CF | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR18 PSIS | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR18 PSIS | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR18 PSIS | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR18 PSIS CF | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR18 PSIS CF | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR18 PSIS CF | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_P0 | System Intact | P0 | No | No | No | No | No | No | No | Non-convergence is observed in the dispatching of Group 05 generators to create the base case. | Line - Woodward - Crawfish Draw 765 kV New Line Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_P0 | System Intact | P0 | No | No | No | No | No | No | No | Non-convergence is observed in the dispatching of Group 05 generators to create the base case. | Line - Woodward - Crawfish Draw 765 kV New Line Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_001 | 3PH Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.4. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_010 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage was observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_069 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | No | Yes | Yes | Yes | Low voltage was observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_127 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.00 (515375) 345.0 kV to WWRDEHV9 765.00 (515378) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_003 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations in TOLK (525561, 525562) units along with reactive power oscillations in Tolk (525561, 525562) and G21-090 (766125) unit were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_006 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_051 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations in G24-GEN261 (784804, 784805),G24-265 (784924, 784925), and TOLK (525561, 525562) units along with reactive power oscillations in Tolk (525561) units were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_113 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations in G24-GEN261 (784804, 784805) and G24-265 (784924, 784925) units along with reactive power oscillations in Tolk (525561) units were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_127 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.00 (515375) 345.0 kV to WWRDEHV9 765.00 (515378) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations were observed in TOLK 1 (525561) in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_010 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_011 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_012 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_120 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case with simulation crashing in base case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_014 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_002 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_008 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT1 118.000 (527901) 18.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_017 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_018 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_019 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_006 | 3PH Phase fault on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELK_CT1 345.00 (525850) 345.0 kV to ELK_2 1 18.000 (525845) 18.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 345.00 (525850) 345.0 kV to ELK_1 118.000 (525844) 18.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_007 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2020-008345.00 (764980) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2021-021345.00 (765490) 345.0 kV Transmission Circuit #1 b.4. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.5. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_016 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. TOLK 7345.00 (525549) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_017 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.7. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.8. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.9. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.10. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.11. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.12. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.13. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.14. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.15. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_037 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.3. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.4. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_002 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_003 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_004 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_001 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_002 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_003 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_004 | 3PH Phase fault on W_HOBBS 3115.00 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3115.00 (528498) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 112.470 (528490) 12.5 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.4. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. W_HOBBS 3115.00 (528498) 115.0 kV to DRINKARD_TP3115.00 (528533) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_005 | 3PH Phase fault on TAYLOR 3115.00 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3115.00 (528413) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. TAYLOR 3115.00 (528413) 115.0 kV to E_SANGER 3115.00 (528470) 115.0 kV Transmission Circuit #1 b.3. SANGER_SW 3115.00 (528463) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.4. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. JOHNSON_DRW3115.00 (527362) 115.0 kV to TAYLOR 3115.00 (528413) 115.0 kV Transmission Circuit #1 b.6. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.7. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.8. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.9. TAYLOR 3115.00 (528413) 115.0 kV to W_BENDER 3115.00 (528449) 115.0 kV Transmission Circuit #1 b.10. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.11. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_006 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_007 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_050 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_009 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.5. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_106 | 3PH Phase fault on MILLEN_TPE 3115.00 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3115.00 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations were observed in transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_005 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_011 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. G24-015-TAP 230.00 (777420) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_012 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.3. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.5. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.6. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_013 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_005 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and power oscillations in G24-GEN261 (784804, 784805) and G24-265 (784924, 784925) units along with reactive power oscillations in Tolk (525561,525562) units were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_001 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.3. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.4. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles and removing reclosing resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_016 | 3PH Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 b.2. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_020 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_021 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_022 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_018 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.16. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.17. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.18. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.19. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_019 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_020 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_023 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_009 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_010 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_011 | 3PH Phase fault on GRPLNS-CB2-134.500 (523126) 34 kV Bus a. Apply fault at the GRPLNS-CB2-134.500 (523126) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-WT2-10.5750 (523123) 0.6 kV Transmission Circuit #1 b.2. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-LV4-134.500 (523127) 34.5 kV to GRPLNS-GT4-10.4800 (523133) 0.5 kV Transmission Circuit #1 b.4. GRPLNS-LV2-134.500 (523129) 34.5 kV to GRPLNS-GT2-10.4800 (523132) 0.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.8. NBLWND-LV2 134.500 (523128) 34.5 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.9. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-WT4-10.5750 (523121) 0.6 kV Transmission Circuit #1 b.10. GRPLNS-HV2-3115.00 (523131) 115.0 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.11. NOBLE_WND 3115.00 (523103) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.12. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_021 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_001 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to PALDR1W7 345.00 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_023 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_024 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_015 | 3PH Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL1 7345.00 (527666) 345.0 kV Transmission Circuit #1 b.2. RSVLT_GEN1 10.6900 (527651) 0.7 kV to RSVLT_WIND1134.500 (527658) 34.5 kV Transmission Circuit #1 b.3. RSVLT_GEN2 10.6900 (527652) 0.7 kV to RSVLT_WIND2134.500 (527659) 34.5 kV Transmission Circuit #1 b.4. RSVLT_WIND1134.500 (527658) 34.5 kV to RSVLT_COL1 134.500 (527660) 34.5 kV Transmission Circuit #1 b.5. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.6. RSVLT_CC_E 7345.00 (527655) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.7. MILO_WIND 10.7000 (527653) 0.7 kV to MILO_CB 34.500 (577120) 34.5 kV Transmission Circuit #1 b.8. MPT3 PRI 34.500 (577121) 34.5 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.9. MILO_WIND 7345.00 (527640) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.11. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL2 7345.00 (527667) 345.0 kV Transmission Circuit #1 b.12. RSVLT_WIND2134.500 (527659) 34.5 kV to RSVLT_COL2 134.500 (527661) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_014 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_015 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_025 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT2 118.000 (527902) 18.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_026 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_027 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT3 118.000 (527903) 18.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_028 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_029 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_030 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_016 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_017 | 3PH Phase fault on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_031 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WARD 3115.00 (528519) 115.0 kV to WHITTEN 3115.00 (528540) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_008 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_019 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_020 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_021 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_032 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_033 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX_2 113.800 (528362) 13.8 kV Transmission Circuit #1 b.3. MADDOX_3 112.500 (528363) 12.5 kV to MADDOXG23 3115.00 (528353) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_022 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to BUCKNER7 345.00 (531501) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_023 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to SETAB 7 345.00 (531465) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_034 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_035 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_036 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.3. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.4. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_024 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_047 | 3PH Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_025 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_038 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_054 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_002 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Protection relay trips were observed in the transfer case with simulation crashing in base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_058 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_004 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_005 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_060 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_013 | 3PH Phase fault on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_008 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_009 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_010 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 b.2. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_011 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_012 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_013 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_014 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_015 | 3PH Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_016 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_079 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_018 | 3PH Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 b.2. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_019 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_020 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case with simulation crashing in base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_021 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_022 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 b.3. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.4. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_023 | 3PH Phase fault on RUSSELL 3115.00 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3115.00 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_024 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_025 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_026 | 3PH Phase fault on NE_HOBBS 3115.00 (528442) 115 kV Bus a. Apply fault at the NE_HOBBS 3115.00 (528442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.3. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.4. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.5. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.6. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.7. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.8. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_027 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.3. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.4. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_028 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_029 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_030 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_031 | 3PH Phase fault on LE-TXACO_TP3115.00 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3115.00 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.3. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.4. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.5. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.6. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.7. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.8. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.9. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.10. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.11. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.12. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_032 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.3. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.4. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.5. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.6. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 b.7. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.8. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.9. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.10. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.11. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.12. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_033 | 3PH Phase fault on JOHNSON_DRW3115.00 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3115.00 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_034 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.4. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.5. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_035 | 3PH Phase fault on XTO_BULLDOG3115.00 (528396) 115 kV Bus a. Apply fault at the XTO_BULLDOG3115.00 (528396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.4. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_036 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.3. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.4. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_117 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_007 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in Gains (527001, 527002) units were identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_017 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area were identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_040 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_041 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_042 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_043 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_111 | 3PH Phase fault on G24-043-TAP 345.00 (778260) 345 kV Bus a. Apply fault at the G24-043-TAP 345.00 (778260) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_116 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_029 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_003 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_048 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_049 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case with simulation crashing in base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_020 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_044 | 3PH Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_052 | 3PH Phase fault on ALLRED_SUB 3115.00 (527024) 115 kV Bus a. Apply fault at the ALLRED_SUB 3115.00 (527024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_053 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_096 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case and in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_055 | 3PH Phase fault on ALRDCRTZ_TP3115.00 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3115.00 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 b.2. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_056 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_057 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_001 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.3. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.4. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_059 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_004 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_037 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_007 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_063 | 3PH Phase fault on EDDY_STH 3115.00 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3115.00 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 b.2. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_064 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_065 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_066 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_067 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_068 | 3PH Phase fault on C1_MPT_PRI 3115.00 (527845) 115 kV Bus a. Apply fault at the C1_MPT_PRI 3115.00 (527845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 b.2. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_008 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_070 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_071 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_038 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_073 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_074 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_075 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_076 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_077 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_078 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_039 | 3PH Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 b.3. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.4. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_009 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_081 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_082 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_006 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_061 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_072 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_015 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Protection relay trips and power oscillations in G24-GEN261 (784804, 784805),G24-265 (784924, 784925), and TOLK (525561, 525562) units along with reactive power oscillations in Tolk (525561) units were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_045 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_084 | 3PH Phase fault on PHANTOM 9765.00 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9765.00 (528014) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_089 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_090 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_046 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_109 | 3PH Phase fault on ANDREWS 6345.00 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6345.00 (528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | Yes | Yes | No | Yes | Protection relay trips and power oscillations in G24-GEN261 (784804, 784805),G24-265 (784924, 784925), and TOLK (525561, 525562) units along with reactive power oscillations in Tolk (525561) and Elk (525844, 525845, 525846) units were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_093 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_094 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_096 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trip and reactive power oscillations in Tolk (525561) unit were identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_096 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_097 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_098 | 3PH Phase fault on BUCKEYE 3115.00 (528385) 115 kV Bus a. Apply fault at the BUCKEYE 3115.00 (528385) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_099 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_100 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_101 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_102 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_103 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEANTL_345 345.00 (528400) 345.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_104 | 3PH Phase fault on MILLEN_TPW 3115.00 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3115.00 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_105 | 3PH Phase fault on MILLEN 3115.00 (528435) 115 kV Bus a. Apply fault at the MILLEN 3115.00 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_092 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in ASGI10-010 (528331) units were identified in the transfer case not in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Rotor angle instability is identified in the transfer case. This behavior is also observed in base case. It is found that the CQ unit do not impact the issue.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_107 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_108 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_007 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in Gains (527001, 527002, 527003) units were identified in the transfer case not in base case with a PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Build a 239.2-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_110 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 269.000 (528617) 69.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_127 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.00 (515375) 345.0 kV to WWRDEHV9 765.00 (515378) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations in Tolk (525561, 525562), Elk (525844, 525845, 525846), and G24-221 (783604) units were observed in the transfer case with a PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_046 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and removing reclosing and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Build a 239.2-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_004 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_085 | 3PH Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 b.2. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_115 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_006 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_088 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_118 | 3PH Phase fault on EDDY_NTH 3115.00 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3115.00 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_119 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_114 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_121 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_122 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_123 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_124 | 3PH Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_125 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_126 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_011 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_017 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_037 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_038 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_022 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_023 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_049 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_074 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_075 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_076 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_077 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_007 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_009 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_022 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_023 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_002 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_011 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_017 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_024 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_025 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_049 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_051 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_074 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_075 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_076 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_078 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_079 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_080 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_082 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_083 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_084 | 3PH Phase fault on PHANTOM 9765.00 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9765.00 (528014) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_085 | 3PH Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 b.2. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_087 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_090 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_109 | 3PH Phase fault on ANDREWS 6345.00 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6345.00 (528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_003 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_004 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_005 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_008 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_015 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_002 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_002 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_003 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_005 | 3PH Phase fault on TAYLOR 3115.00 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3115.00 (528413) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. TAYLOR 3115.00 (528413) 115.0 kV to E_SANGER 3115.00 (528470) 115.0 kV Transmission Circuit #1 b.3. SANGER_SW 3115.00 (528463) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.4. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. JOHNSON_DRW3115.00 (527362) 115.0 kV to TAYLOR 3115.00 (528413) 115.0 kV Transmission Circuit #1 b.6. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.7. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.8. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.9. TAYLOR 3115.00 (528413) 115.0 kV to W_BENDER 3115.00 (528449) 115.0 kV Transmission Circuit #1 b.10. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.11. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_006 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_007 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_008 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT1 118.000 (527901) 18.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_012 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.3. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.5. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.6. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_013 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_014 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_021 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_012 | 3PH Phase fault on SPNSPUR_WND134.500 (524294) 34 kV Bus a. Apply fault at the SPNSPUR_WND134.500 (524294) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPNSPUR_WND7345.00 (524296) 345.0 kV to SPNSPUR_COL7345.00 (524299) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.3. BECKHAM7 345.00 (516059) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #2 b.4. SPNSPUR_GEN10.6900 (524295) 0.7 kV to SPNSPUR_WND134.500 (524294) 34.5 kV Transmission Circuit #1 b.5. POTTER_CO 7345.00 (523961) 345.0 kV to SPNSPUR_WND7345.00 (524296) 345.0 kV Transmission Circuit #1 b.6. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_023 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_024 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_025 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT2 118.000 (527902) 18.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_026 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_027 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT3 118.000 (527903) 18.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_032 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_036 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.3. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.4. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_038 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_027 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.3. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.4. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_038 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_045 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_061 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_077 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_089 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_113 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_006 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_058 | 3PH Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_001 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.3. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.4. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reduction of clearing time to 5 cycles with no reclosing resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_001 | 3PH Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.4. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_002 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_006 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_010 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_011 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_012 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_013 | 3PH Phase fault on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_014 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_016 | 3PH Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 b.2. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_017 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_018 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_019 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_020 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P1_FAULT_021 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_001 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to PALDR1W7 345.00 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_003 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_004 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_001 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_004 | 3PH Phase fault on W_HOBBS 3115.00 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3115.00 (528498) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 112.470 (528490) 12.5 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.4. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. W_HOBBS 3115.00 (528498) 115.0 kV to DRINKARD_TP3115.00 (528533) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_009 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.5. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_010 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_005 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_011 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. G24-015-TAP 230.00 (777420) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_006 | 3PH Phase fault on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELK_CT1 345.00 (525850) 345.0 kV to ELK_2 1 18.000 (525845) 18.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 345.00 (525850) 345.0 kV to ELK_1 118.000 (525844) 18.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_007 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2020-008345.00 (764980) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2021-021345.00 (765490) 345.0 kV Transmission Circuit #1 b.4. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.5. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_015 | 3PH Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL1 7345.00 (527666) 345.0 kV Transmission Circuit #1 b.2. RSVLT_GEN1 10.6900 (527651) 0.7 kV to RSVLT_WIND1134.500 (527658) 34.5 kV Transmission Circuit #1 b.3. RSVLT_GEN2 10.6900 (527652) 0.7 kV to RSVLT_WIND2134.500 (527659) 34.5 kV Transmission Circuit #1 b.4. RSVLT_WIND1134.500 (527658) 34.5 kV to RSVLT_COL1 134.500 (527660) 34.5 kV Transmission Circuit #1 b.5. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.6. RSVLT_CC_E 7345.00 (527655) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.7. MILO_WIND 10.7000 (527653) 0.7 kV to MILO_CB 34.500 (577120) 34.5 kV Transmission Circuit #1 b.8. MPT3 PRI 34.500 (577121) 34.5 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.9. MILO_WIND 7345.00 (527640) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.11. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL2 7345.00 (527667) 345.0 kV Transmission Circuit #1 b.12. RSVLT_WIND2134.500 (527659) 34.5 kV to RSVLT_COL2 134.500 (527661) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_016 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. TOLK 7345.00 (525549) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_017 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.7. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.8. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.9. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.10. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.11. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.12. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.13. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.14. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.15. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_018 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.16. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.17. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.18. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.19. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_019 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_020 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_008 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_009 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_010 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_011 | 3PH Phase fault on GRPLNS-CB2-134.500 (523126) 34 kV Bus a. Apply fault at the GRPLNS-CB2-134.500 (523126) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-WT2-10.5750 (523123) 0.6 kV Transmission Circuit #1 b.2. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-LV4-134.500 (523127) 34.5 kV to GRPLNS-GT4-10.4800 (523133) 0.5 kV Transmission Circuit #1 b.4. GRPLNS-LV2-134.500 (523129) 34.5 kV to GRPLNS-GT2-10.4800 (523132) 0.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.8. NBLWND-LV2 134.500 (523128) 34.5 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.9. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-WT4-10.5750 (523121) 0.6 kV Transmission Circuit #1 b.10. GRPLNS-HV2-3115.00 (523131) 115.0 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.11. NOBLE_WND 3115.00 (523103) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.12. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_013 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_014 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_015 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_028 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_030 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_016 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_017 | 3PH Phase fault on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_031 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WARD 3115.00 (528519) 115.0 kV to WHITTEN 3115.00 (528540) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_018 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. TUCO_INT 6230.00 (525830) 230.0 kV to JONES 6230.00 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 6230.00 (525830) 230.0 kV to CARLISLE 6230.00 (526161) 230.0 kV Transmission Circuit #1 b.4. O.K.U.2-7 345.00 (511584) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.5. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.6. TUCO_INT 6230.00 (525830) 230.0 kV to HALE_WNDCL16230.00 (525957) 230.0 kV Transmission Circuit #1 b.7. TOLK 6230.00 (525531) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 b.8. SWISHER 6230.00 (525213) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_019 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_020 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_021 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_033 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX_2 113.800 (528362) 13.8 kV Transmission Circuit #1 b.3. MADDOX_3 112.500 (528363) 12.5 kV to MADDOXG23 3115.00 (528353) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_022 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to BUCKNER7 345.00 (531501) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_023 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to SETAB 7 345.00 (531465) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_035 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_037 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.3. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.4. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_024 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_025 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_004 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_005 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_008 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_009 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_010 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 b.2. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_012 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_013 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_014 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_015 | 3PH Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_016 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_018 | 3PH Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 b.2. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_019 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_021 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_022 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 b.3. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.4. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_023 | 3PH Phase fault on RUSSELL 3115.00 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3115.00 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_026 | 3PH Phase fault on NE_HOBBS 3115.00 (528442) 115 kV Bus a. Apply fault at the NE_HOBBS 3115.00 (528442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.3. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.4. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.5. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.6. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.7. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.8. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_028 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_029 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_030 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_031 | 3PH Phase fault on LE-TXACO_TP3115.00 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3115.00 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.3. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.4. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.5. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.6. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.7. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.8. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.9. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.10. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.11. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.12. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_032 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.3. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.4. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.5. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.6. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 b.7. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.8. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.9. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.10. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.11. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.12. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_033 | 3PH Phase fault on JOHNSON_DRW3115.00 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3115.00 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_034 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.4. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.5. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_035 | 3PH Phase fault on XTO_BULLDOG3115.00 (528396) 115 kV Bus a. Apply fault at the XTO_BULLDOG3115.00 (528396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.4. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_036 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.3. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.4. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_037 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_039 | 3PH Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 b.3. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.4. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_040 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_041 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_042 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_043 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_047 | 3PH Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_048 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_050 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_052 | 3PH Phase fault on ALLRED_SUB 3115.00 (527024) 115 kV Bus a. Apply fault at the ALLRED_SUB 3115.00 (527024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_053 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_054 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_055 | 3PH Phase fault on ALRDCRTZ_TP3115.00 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3115.00 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 b.2. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_056 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_057 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_059 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_060 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_063 | 3PH Phase fault on EDDY_STH 3115.00 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3115.00 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 b.2. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_064 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_065 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_066 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_067 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_068 | 3PH Phase fault on C1_MPT_PRI 3115.00 (527845) 115 kV Bus a. Apply fault at the C1_MPT_PRI 3115.00 (527845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 b.2. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_069 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_070 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_071 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_072 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_073 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_081 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_086 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_088 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_091 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_092 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_093 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_094 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_095 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_097 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_098 | 3PH Phase fault on BUCKEYE 3115.00 (528385) 115 kV Bus a. Apply fault at the BUCKEYE 3115.00 (528385) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_099 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_100 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_101 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_102 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_103 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEANTL_345 345.00 (528400) 345.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_104 | 3PH Phase fault on MILLEN_TPW 3115.00 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3115.00 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_105 | 3PH Phase fault on MILLEN 3115.00 (528435) 115 kV Bus a. Apply fault at the MILLEN 3115.00 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_106 | 3PH Phase fault on MILLEN_TPE 3115.00 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3115.00 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_107 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_108 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_110 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 269.000 (528617) 69.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_111 | 3PH Phase fault on G24-043-TAP 345.00 (778260) 345 kV Bus a. Apply fault at the G24-043-TAP 345.00 (778260) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_114 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_115 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_116 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_117 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_118 | 3PH Phase fault on EDDY_NTH 3115.00 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3115.00 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_119 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_120 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_121 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_122 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_123 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_124 | 3PH Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_125 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_126 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_059 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_060 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_054 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_116 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_020 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_043 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_078 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_018 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. TUCO_INT 6230.00 (525830) 230.0 kV to JONES 6230.00 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 6230.00 (525830) 230.0 kV to CARLISLE 6230.00 (526161) 230.0 kV Transmission Circuit #1 b.4. O.K.U.2-7 345.00 (511584) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.5. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.6. TUCO_INT 6230.00 (525830) 230.0 kV to HALE_WNDCL16230.00 (525957) 230.0 kV Transmission Circuit #1 b.7. TOLK 6230.00 (525531) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 b.8. SWISHER 6230.00 (525213) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips and oscillations were observed in the transfer case and in the base case. The CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_058 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes |  | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_005 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_009 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_015 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_109 | 3PH Phase fault on ANDREWS 6345.00 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6345.00 (528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | No | Yes | Protection relay trips and oscillations were observed in the transfer case and in the base case. The CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_002 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_009 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_013 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_014 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_018 | 3PH Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 b.2. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_047 | 3PH Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_051 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_065 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_067 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_103 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEANTL_345 345.00 (528400) 345.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_111 | 3PH Phase fault on G24-043-TAP 345.00 (778260) 345 kV Bus a. Apply fault at the G24-043-TAP 345.00 (778260) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_115 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_118 | 3PH Phase fault on EDDY_NTH 3115.00 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3115.00 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_119 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_123 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_124 | 3PH Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_125 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_006 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_007 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_019 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_008 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_022 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to BUCKNER7 345.00 (531501) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_023 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to SETAB 7 345.00 (531465) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_016 | 3PH Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 b.2. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_024 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | No | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_007 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_013 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_035 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_036 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.3. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.4. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_082 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_024 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_001 | 3PH Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.4. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_002 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_003 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_005 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_010 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 b.2. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_015 | 3PH Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_010 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_011 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_021 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_022 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 b.3. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.4. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_023 | 3PH Phase fault on RUSSELL 3115.00 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3115.00 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_025 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_026 | 3PH Phase fault on NE_HOBBS 3115.00 (528442) 115 kV Bus a. Apply fault at the NE_HOBBS 3115.00 (528442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.3. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.4. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.5. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.6. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.7. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.8. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_028 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_029 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_030 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_032 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.3. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.4. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.5. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.6. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 b.7. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.8. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.9. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.10. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.11. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.12. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_033 | 3PH Phase fault on JOHNSON_DRW3115.00 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3115.00 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_034 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.4. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.5. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_035 | 3PH Phase fault on XTO_BULLDOG3115.00 (528396) 115 kV Bus a. Apply fault at the XTO_BULLDOG3115.00 (528396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.4. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_036 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.3. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.4. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_040 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_041 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_042 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_012 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_014 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_015 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_017 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_018 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_020 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_021 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_048 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_050 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_052 | 3PH Phase fault on ALLRED_SUB 3115.00 (527024) 115 kV Bus a. Apply fault at the ALLRED_SUB 3115.00 (527024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_053 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_055 | 3PH Phase fault on ALRDCRTZ_TP3115.00 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3115.00 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 b.2. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_056 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_057 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_063 | 3PH Phase fault on EDDY_STH 3115.00 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3115.00 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 b.2. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_064 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_066 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_068 | 3PH Phase fault on C1_MPT_PRI 3115.00 (527845) 115 kV Bus a. Apply fault at the C1_MPT_PRI 3115.00 (527845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 b.2. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_069 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_070 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_071 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_073 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_081 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_093 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_094 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_097 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_098 | 3PH Phase fault on BUCKEYE 3115.00 (528385) 115 kV Bus a. Apply fault at the BUCKEYE 3115.00 (528385) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_099 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_100 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_101 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_102 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_104 | 3PH Phase fault on MILLEN_TPW 3115.00 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3115.00 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_105 | 3PH Phase fault on MILLEN 3115.00 (528435) 115 kV Bus a. Apply fault at the MILLEN 3115.00 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_106 | 3PH Phase fault on MILLEN_TPE 3115.00 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3115.00 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_107 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_108 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_110 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 269.000 (528617) 69.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_126 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_003 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_004 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_001 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_004 | 3PH Phase fault on W_HOBBS 3115.00 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3115.00 (528498) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 112.470 (528490) 12.5 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.4. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. W_HOBBS 3115.00 (528498) 115.0 kV to DRINKARD_TP3115.00 (528533) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_005 | 3PH Phase fault on TAYLOR 3115.00 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3115.00 (528413) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. TAYLOR 3115.00 (528413) 115.0 kV to E_SANGER 3115.00 (528470) 115.0 kV Transmission Circuit #1 b.3. SANGER_SW 3115.00 (528463) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.4. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. JOHNSON_DRW3115.00 (527362) 115.0 kV to TAYLOR 3115.00 (528413) 115.0 kV Transmission Circuit #1 b.6. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.7. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.8. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.9. TAYLOR 3115.00 (528413) 115.0 kV to W_BENDER 3115.00 (528449) 115.0 kV Transmission Circuit #1 b.10. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.11. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_008 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT1 118.000 (527901) 18.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_009 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.5. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_005 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_011 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. G24-015-TAP 230.00 (777420) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_006 | 3PH Phase fault on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELK_CT1 345.00 (525850) 345.0 kV to ELK_2 1 18.000 (525845) 18.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 345.00 (525850) 345.0 kV to ELK_1 118.000 (525844) 18.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_007 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2020-008345.00 (764980) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2021-021345.00 (765490) 345.0 kV Transmission Circuit #1 b.4. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.5. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_019 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_020 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_010 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_011 | 3PH Phase fault on GRPLNS-CB2-134.500 (523126) 34 kV Bus a. Apply fault at the GRPLNS-CB2-134.500 (523126) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-WT2-10.5750 (523123) 0.6 kV Transmission Circuit #1 b.2. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-LV4-134.500 (523127) 34.5 kV to GRPLNS-GT4-10.4800 (523133) 0.5 kV Transmission Circuit #1 b.4. GRPLNS-LV2-134.500 (523129) 34.5 kV to GRPLNS-GT2-10.4800 (523132) 0.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.8. NBLWND-LV2 134.500 (523128) 34.5 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.9. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-WT4-10.5750 (523121) 0.6 kV Transmission Circuit #1 b.10. GRPLNS-HV2-3115.00 (523131) 115.0 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.11. NOBLE_WND 3115.00 (523103) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.12. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_014 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_025 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT2 118.000 (527902) 18.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_027 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT3 118.000 (527903) 18.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_028 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_030 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_016 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_017 | 3PH Phase fault on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_031 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WARD 3115.00 (528519) 115.0 kV to WHITTEN 3115.00 (528540) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_019 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_020 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_021 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_032 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_033 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX_2 113.800 (528362) 13.8 kV Transmission Circuit #1 b.3. MADDOX_3 112.500 (528363) 12.5 kV to MADDOXG23 3115.00 (528353) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_037 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.3. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.4. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_025 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_027 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.3. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.4. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_031 | 3PH Phase fault on LE-TXACO_TP3115.00 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3115.00 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.3. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.4. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.5. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.6. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.7. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.8. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.9. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.10. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.11. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.12. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_013 | 3PH Phase fault on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_001 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to PALDR1W7 345.00 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_002 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_006 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_012 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.3. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.5. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.6. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_015 | 3PH Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL1 7345.00 (527666) 345.0 kV Transmission Circuit #1 b.2. RSVLT_GEN1 10.6900 (527651) 0.7 kV to RSVLT_WIND1134.500 (527658) 34.5 kV Transmission Circuit #1 b.3. RSVLT_GEN2 10.6900 (527652) 0.7 kV to RSVLT_WIND2134.500 (527659) 34.5 kV Transmission Circuit #1 b.4. RSVLT_WIND1134.500 (527658) 34.5 kV to RSVLT_COL1 134.500 (527660) 34.5 kV Transmission Circuit #1 b.5. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.6. RSVLT_CC_E 7345.00 (527655) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.7. MILO_WIND 10.7000 (527653) 0.7 kV to MILO_CB 34.500 (577120) 34.5 kV Transmission Circuit #1 b.8. MPT3 PRI 34.500 (577121) 34.5 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.9. MILO_WIND 7345.00 (527640) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.11. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL2 7345.00 (527667) 345.0 kV Transmission Circuit #1 b.12. RSVLT_WIND2134.500 (527659) 34.5 kV to RSVLT_COL2 134.500 (527661) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_023 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_024 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_026 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_029 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_016 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. TOLK 7345.00 (525549) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_017 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.7. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.8. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.9. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.10. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.11. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.12. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.13. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.14. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.15. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_018 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.16. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.17. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.18. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.19. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_072 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_003 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_004 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_095 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in Maddox (528362) unit was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_006 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_090 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_120 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_121 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_014 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_012 | 3PH Phase fault on SPNSPUR_WND134.500 (524294) 34 kV Bus a. Apply fault at the SPNSPUR_WND134.500 (524294) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPNSPUR_WND7345.00 (524296) 345.0 kV to SPNSPUR_COL7345.00 (524299) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.3. BECKHAM7 345.00 (516059) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #2 b.4. SPNSPUR_GEN10.6900 (524295) 0.7 kV to SPNSPUR_WND134.500 (524294) 34.5 kV Transmission Circuit #1 b.5. POTTER_CO 7345.00 (523961) 345.0 kV to SPNSPUR_WND7345.00 (524296) 345.0 kV Transmission Circuit #1 b.6. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_021 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_002 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_034 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_001 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.2. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.3. PHANTOM 7345.00 (528015) 345.0 kV to CHINA_DRAW 7345.00 (528223) 345.0 kV Transmission Circuit #1 b.4. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_003 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_004 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_009 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_044 | 3PH Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_062 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_079 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_080 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_083 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_087 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_089 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_084 | 3PH Phase fault on PHANTOM 9765.00 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9765.00 (528014) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_085 | 3PH Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 b.2. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_061 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_003 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P4_FAULT_014 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_012 | 3PH Phase fault on SPNSPUR_WND134.500 (524294) 34 kV Bus a. Apply fault at the SPNSPUR_WND134.500 (524294) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPNSPUR_WND7345.00 (524296) 345.0 kV to SPNSPUR_COL7345.00 (524299) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.3. BECKHAM7 345.00 (516059) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #2 b.4. SPNSPUR_GEN10.6900 (524295) 0.7 kV to SPNSPUR_WND134.500 (524294) 34.5 kV Transmission Circuit #1 b.5. POTTER_CO 7345.00 (523961) 345.0 kV to SPNSPUR_WND7345.00 (524296) 345.0 kV Transmission Circuit #1 b.6. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_013 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_REGIONAL_P4_FAULT_018 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. TUCO_INT 6230.00 (525830) 230.0 kV to JONES 6230.00 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 6230.00 (525830) 230.0 kV to CARLISLE 6230.00 (526161) 230.0 kV Transmission Circuit #1 b.4. O.K.U.2-7 345.00 (511584) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.5. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.6. TUCO_INT 6230.00 (525830) 230.0 kV to HALE_WNDCL16230.00 (525957) 230.0 kV Transmission Circuit #1 b.7. TOLK 6230.00 (525531) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 b.8. SWISHER 6230.00 (525213) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_003 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to N_LOVING 7345.00 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_044 | 3PH Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_062 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_080 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_083 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_086 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_087 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_091 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_092 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_095 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_112 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_007 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_013 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. This behavior was also observed in the base case. The CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_007 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in Gains (527001, 527002, 527003) and EPTNP (599961) units were identified in the transfer case not in base case with a PTDF >3%. | The transfer case requires the following removed upgrades for the CF Analysis to be reapplied in the transfer case as well as a clearing time of 4 cycles with no reclosing. Potter to Tolk 345 kV Double Circuit Line Build Build New Beckham to Potter 345 kV Line Ckt 2 Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV XFR - Hobbs 230/115 kV Build New Andrews to Road Runner 345 kV Line
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_012 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 4 cycles resolves the issue. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_045 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_046 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_122 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. This behavior was also observed in the base case. The CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_038 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. This behavior was also observed in the base case. The CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_062 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29S | Transfer Case | GROUP05_LOCAL_P1_FAULT_112 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor instability was observed in transfer case. This behavior was also observed in the base case. PTDF is less than 3% and CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_010 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Steady state low voltage is observed in transfer case. This is also observed in base case. The CQ unit do not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_008 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing the fault clearing to 5 cycles shows that the same behavior in transfer and base case. The CQ unit is shown to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_016 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_039 | 3PH Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 b.3. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.4. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power, frequency, and reactive power oscillations including Hobbs were observed in transfer case. Reducing the clearing time to 4 cycles resolves the issue. | Reducing the clearing time to 4 cycles resolves the issue. The base case was found to the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_019 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_112 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. This behavior was also observed in the base case. The CQ units were found to not impact the issue. | No mitigation is required.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_113 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations in Tolk (525561, 525562), Gaines (527003), Maddox (528362), and Hobbs (527901) as well as reactive power oscillations in tolk (525561, 525562) and Elk (525844, 525845, 525846) units were observed in the transfer case. | Upgrades required: Line - Woodward - Crawfish Draw 765 kV New Line Line - Crawfish Draw - Phantom 765 kV New Line Crawfish Draw - Phantom 765 kV New Ckt 2 Line Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_117 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trips was observed in the transfer case. The CQ units were found to not impact the issue. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_044 | 3PH Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles with no reclosing resolves the issue. | Reduction of clearing time to 5 cycles with no reclosing resolves the issue. Base case was found to require the same clearing time with no reclosing.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_046 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | The transfer case requires the removed Project: Potter to Tolk 345 kV Double Circuit Line Build, to be reapplied in the transfer case as well as a clearing time of 5 cycles with no reclosing to resolve the issue. Base case was found to require the same clearing time and upgrade.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_022 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case.. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_023 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to G24-041-TAP 345.00 (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case.. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_062 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles with no reclosing resolves the issue. | Reduction of clearing time to 5 cycles with no reclosing resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_011 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power, voltage, frequency, and reactive power oscillations in several units including Hobbs (527903) unit were observed in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_038 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHIL23115.00 (528231) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power, voltage, frequency, and reactive power oscillations in several units including Hobbs (527903) unit were observed in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_079 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in Gaines (527001, 527002) were identified in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_082 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in the base case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_086 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_088 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle instability is identified in the transfer case. This behavior is also observed in base case. It is found that the CQ unit do not impact the issue.
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_008 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in base case with PTDF >3%. | Reducing the fault clearing to 5 cycles and removing reclosing and applying the following upgrades resolved the issue. Upgrades required: Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 119.6 MVAR line reactor at Crawfish Draw 765 kV substation Build a 263.9-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw Install new 345/765 kV Ckt 1 transformer at Woodward Install new 345/765 kV Ckt 2 transformer at Woodward Install 765 kV substation at Viola Install 150 MVAR reactor at Viola 765 kV substation Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola Install new 345/765 kV Ckt 1 transformer at Viola Install new 345/765 kV Ckt 2 transformer at Viola Install new 345/765 kV Ckt 3 transformer at Viola
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_087 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | Yes | Yes | No | Yes | Protection relay trips and reactive power oscillations in Tolk (525562) unit were observed in the transfer case. Reducing clearing time to 5 cycles resolves the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require less clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_088 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_090 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case not in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_001 | 3PH Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.4. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_002 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_003 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_004 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_005 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_006 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_007 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to LAMAR7 345.00 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_008 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_002 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_005 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_009 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_008 | 3PH Phase fault on SIDEWINDER 7345.00 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7345.00 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. SIDEWINDER 7345.00 (527020) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_009 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_010 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 b.2. CHAVES_CNTY6230.00 (527483) 230.0 kV to EDDY_NORTH 6230.00 (527799) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_012 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to MUSTANG 6230.00 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_013 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to 7-RIVERS 6230.00 (528095) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_014 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_015 | 3PH Phase fault on 7-RIVERS 6230.00 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6230.00 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. 7-RIVERS 6230.00 (528095) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_010 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_011 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_016 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to BRU_SUB 6230.00 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_017 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_018 | 3PH Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 b.2. NEEDMORE 6230.00 (525586) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_019 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_020 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_021 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_022 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 b.3. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.4. DENVER_N 3115.00 (527130) 115.0 kV to HIGGEAST 3115.00 (527286) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_023 | 3PH Phase fault on RUSSELL 3115.00 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3115.00 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. RUSSELL 3115.00 (527284) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_024 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_025 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_026 | 3PH Phase fault on NE_HOBBS 3115.00 (528442) 115 kV Bus a. Apply fault at the NE_HOBBS 3115.00 (528442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.3. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.4. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.5. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.6. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.7. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.8. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_027 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.3. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.4. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_028 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_029 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WAITS 3115.00 (528325) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_030 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_031 | 3PH Phase fault on LE-TXACO_TP3115.00 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3115.00 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.3. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.4. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.5. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.6. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.7. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.8. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.9. LE-TXACO_TP3115.00 (528627) 115.0 kV to LE-TEXACO 3115.00 (528792) 115.0 kV Transmission Circuit #1 b.10. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.11. LE-SANANDRS3115.00 (528341) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.12. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_032 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.3. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.4. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.5. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.6. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 b.7. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.8. OIL_CENTER 3115.00 (528552) 115.0 kV to COOPER_RNCH3115.00 (528554) 115.0 kV Transmission Circuit #1 b.9. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.10. COOPER_RNCH3115.00 (528554) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.11. MONUMENT 3115.00 (528491) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #z1 b.12. BYRD_TP 3115.00 (528581) 115.0 kV to BYRD 3115.00 (528582) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_033 | 3PH Phase fault on JOHNSON_DRW3115.00 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3115.00 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_034 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.4. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.5. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_035 | 3PH Phase fault on XTO_BULLDOG3115.00 (528396) 115 kV Bus a. Apply fault at the XTO_BULLDOG3115.00 (528396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.3. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.4. PCA 3115.00 (527930) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_036 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 b.3. BATTLE_AXE 3115.00 (528040) 115.0 kV to ZIAHILS13 3 115.00 (528542) 115.0 kV Transmission Circuit #1 b.4. RDRUNNER 3115.00 (528025) 115.0 kV to BATTLE_AXE 3115.00 (528040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_037 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CUSTERMTN 3115.00 (528239) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_039 | 3PH Phase fault on AGAVE_RHILL3115.00 (528230) 115 kV Bus a. Apply fault at the AGAVE_RHILL3115.00 (528230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.2. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 b.3. RDRUNNER 3115.00 (528025) 115.0 kV to AGAVE_RHILL3115.00 (528230) 115.0 kV Transmission Circuit #1 b.4. AGAVE_RHILL3115.00 (528230) 115.0 kV to OCHOA 3115.00 (528232) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_040 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 b.2. POTASH_JCT 3115.00 (527962) 115.0 kV to KIOWA 3115.00 (527966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_041 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_042 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_043 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_012 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_013 | 3PH Phase fault on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 b.2. OLYMPIA7 345.00 (523040) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_014 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_015 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_016 | 3PH Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 b.2. BUFF_DUNES 7345.00 (523118) 345.0 kV to FINNEY 7345.00 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_017 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_018 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_019 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_091 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle instability in ASGI10-010 (528331) units were identified in the transfer case in the transfer case. This behavior is also observed in base case. It is found that the CQ unit do not impact the issue.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_045 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_047 | 3PH Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. TOLK 7345.00 (525549) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_020 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P1_FAULT_021 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_048 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_049 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6230.00 (526935) 230.0 kV to G24-015-TAP 230.00 (777420) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_050 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_051 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_052 | 3PH Phase fault on ALLRED_SUB 3115.00 (527024) 115 kV Bus a. Apply fault at the ALLRED_SUB 3115.00 (527024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. ALLRED_SUB 3115.00 (527024) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_053 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_054 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_055 | 3PH Phase fault on ALRDCRTZ_TP3115.00 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3115.00 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 b.2. ALRDCRTZ_TP3115.00 (527030) 115.0 kV to XTO_CORNEL+3115.00 (527033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_056 | 3PH Phase fault on HIGGEAST 3115.00 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3115.00 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.2. HIGGEAST 3115.00 (527286) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_057 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_058 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_059 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_060 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_061 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_112 | 3PH Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 765.00 (515378) 765.0 kV to POTTER_CO 9765.00 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles resolves the issue. Base case was found to require the same clearing time.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_063 | 3PH Phase fault on EDDY_STH 3115.00 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3115.00 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 b.2. EDDY_STH 3115.00 (527793) 115.0 kV to EDDY_NTH 3115.00 (527798) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_064 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_065 | 3PH Phase fault on EDDY_NORTH 6230.00 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6230.00 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 b.2. EDDY_NORTH 6230.00 (527799) 230.0 kV to EPTNP-D6 230.00 (599960) 230.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_066 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_067 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_068 | 3PH Phase fault on C1_MPT_PRI 3115.00 (527845) 115 kV Bus a. Apply fault at the C1_MPT_PRI 3115.00 (527845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 b.2. C1_MPT_PRI 3115.00 (527845) 115.0 kV to CUNNINHAM 3115.00 (527864) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_069 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to BUCKEYE_TP 3115.00 (528348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_070 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to QUAHADA 3115.00 (528394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_071 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_072 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_073 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_074 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_075 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_076 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_077 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_078 | 3PH Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_081 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_084 | 3PH Phase fault on PHANTOM 9765.00 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9765.00 (528014) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_085 | 3PH Phase fault on RR_SVC_HV 3115.00 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3115.00 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 b.2. RR_SVC_HV 3115.00 (528024) 115.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_086 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 b.2. RDRUNNER 3115.00 (528025) 115.0 kV to CPERHEAD_HV3115.00 (528033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_089 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_114 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case and simulation crashes after fault in the base case. Reducing clearing time to 5 cycles in transfer and base case shows that the CQ unit do not impact the issue. | Reduction of clearing time to 5 cycles in transfer and base case indicate that issues observed are not worsened by the CQ units.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_091 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_092 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_093 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to BUCKEYE 3115.00 (528385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_094 | 3PH Phase fault on BUCKEYE_TP 3115.00 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3115.00 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE_TP 3115.00 (528348) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_095 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_096 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_097 | 3PH Phase fault on MADDOX 3115.00 (528355) 115 kV Bus a. Apply fault at the MADDOX 3115.00 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_098 | 3PH Phase fault on BUCKEYE 3115.00 (528385) 115 kV Bus a. Apply fault at the BUCKEYE 3115.00 (528385) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 b.2. BUCKEYE 3115.00 (528385) 115.0 kV to LE-TXACO_TP3115.00 (528627) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_099 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_100 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to XTO_BULLDOG3115.00 (528396) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_101 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_102 | 3PH Phase fault on QUAHADA 3115.00 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3115.00 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.2. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_103 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEANTL_345 345.00 (528400) 345.0 kV to LEA_NATIONL3115.00 (528399) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_104 | 3PH Phase fault on MILLEN_TPW 3115.00 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3115.00 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.2. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_105 | 3PH Phase fault on MILLEN 3115.00 (528435) 115 kV Bus a. Apply fault at the MILLEN 3115.00 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_106 | 3PH Phase fault on MILLEN_TPE 3115.00 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3115.00 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.2. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_107 | 3PH Phase fault on MONUMENT 3115.00 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3115.00 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_108 | 3PH Phase fault on MONUMNT_TP 3115.00 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3115.00 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 b.2. MONUMNT_TP 3115.00 (528568) 115.0 kV to BYRD_TP 3115.00 (528581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_109 | 3PH Phase fault on ANDREWS 6345.00 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6345.00 (528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_110 | 3PH Phase fault on LE-WAITS 3115.00 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3115.00 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 269.000 (528617) 69.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_111 | 3PH Phase fault on G24-043-TAP 345.00 (778260) 345 kV Bus a. Apply fault at the G24-043-TAP 345.00 (778260) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 b.2. G24-043-TAP 345.00 (778260) 345.0 kV to G24-109-TAP 345.00 (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_034 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTTER_CO 9765.00 (523966) 765.0 kV to CROSSROADS 9765.00 (527669) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Widespread rotor angle instability in the study area was identified in the transfer case. | The transfer case requires the following removed upgrades for the CF Analysis to be reapplied in the transfer case as well as a clearing time of 4 cycles with no reclosing. Potter to Tolk 345 kV Double Circuit Line Build Build New Beckham to Potter 345 kV Line Ckt 2 Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV XFR - Hobbs 230/115 kV Build New Andrews to Road Runner 345 kV Line
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_113 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_114 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_115 | 3PH Phase fault on CHAVES_CNTY6230.00 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6230.00 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_116 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_117 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_118 | 3PH Phase fault on EDDY_NTH 3115.00 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3115.00 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_119 | 3PH Phase fault on POTASH_JCT 3115.00 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3115.00 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_120 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_121 | 3PH Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Protection relay trips were observed in the transfer case. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_122 | 3PH Phase fault on RDRUNNER 3115.00 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3115.00 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_123 | 3PH Phase fault on BATTLE_AXE 3115.00 (528040) 115 kV Bus a. Apply fault at the BATTLE_AXE 3115.00 (528040) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_124 | 3PH Phase fault on N_LOVING 7345.00 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7345.00 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_125 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_126 | 3PH Phase fault on PEARLE 3115.00 (528392) 115 kV Bus a. Apply fault at the PEARLE 3115.00 (528392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P1_FAULT_127 | 3PH Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.00 (515375) 345.0 kV to WWRDEHV9 765.00 (515378) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_001 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to PALDR1W7 345.00 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_002 | 3PH Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7345.00 (515458) 345.0 kV to BECKHAM7 345.00 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_003 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_004 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_001 | 3PH Phase fault on CUNNIGHM_N 6230.00 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6230.00 (527865) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_002 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.3. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_003 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_004 | 3PH Phase fault on W_HOBBS 3115.00 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3115.00 (528498) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.2. MADDOX 3115.00 (528355) 115.0 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.3. MONUMENT 112.470 (528490) 12.5 kV to MONUMENT 3115.00 (528491) 115.0 kV Transmission Circuit #1 b.4. MONUMENT 3115.00 (528491) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. W_HOBBS 3115.00 (528498) 115.0 kV to DRINKARD_TP3115.00 (528533) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_005 | 3PH Phase fault on TAYLOR 3115.00 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3115.00 (528413) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MILLEN 3115.00 (528435) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.2. TAYLOR 3115.00 (528413) 115.0 kV to E_SANGER 3115.00 (528470) 115.0 kV Transmission Circuit #1 b.3. SANGER_SW 3115.00 (528463) 115.0 kV to G18-004-TAP 115.00 (762442) 115.0 kV Transmission Circuit #1 b.4. SW_4J44 3115.00 (528484) 115.0 kV to W_HOBBS 3115.00 (528498) 115.0 kV Transmission Circuit #1 b.5. JOHNSON_DRW3115.00 (527362) 115.0 kV to TAYLOR 3115.00 (528413) 115.0 kV Transmission Circuit #1 b.6. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN 3115.00 (528435) 115.0 kV Transmission Circuit #*1 b.7. HOBBS_INT 3115.00 (527891) 115.0 kV to MILLEN_TPW 3115.00 (528434) 115.0 kV Transmission Circuit #1 b.8. MILLEN_TPE 3115.00 (528436) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 b.9. TAYLOR 3115.00 (528413) 115.0 kV to W_BENDER 3115.00 (528449) 115.0 kV Transmission Circuit #1 b.10. MILLEN_TPW 3115.00 (528434) 115.0 kV to MILLEN_TPE 3115.00 (528436) 115.0 kV Transmission Circuit #*1 b.11. TAYLOR 3115.00 (528413) 115.0 kV to NE_HOBBS 3115.00 (528442) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_006 | 3PH Phase fault on HIGG 3115.00 (527363) 115 kV Bus a. Apply fault at the HIGG 3115.00 (527363) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. JOHNSON_DRW3115.00 (527362) 115.0 kV to HIGG 3115.00 (527363) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_007 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_008 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT1 118.000 (527901) 18.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_009 | 3PH Phase fault on DCP_ZIA TP 3115.00 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3115.00 (528422) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MALJMAR1&2 3115.00 (528406) 115.0 kV to ZIA 3115.00 (528420) 115.0 kV Transmission Circuit #1 b.2. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.5. ZIA 3115.00 (528420) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.6. DCP_ZIA TP 3115.00 (528422) 115.0 kV to DCP_ZIA 3115.00 (528423) 115.0 kV Transmission Circuit #1 b.7. QUAHADA 3115.00 (528394) 115.0 kV to DCP_ZIA TP 3115.00 (528422) 115.0 kV Transmission Circuit #1 b.8. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_010 | 3PH Phase fault on POTASH_JCT 6230.00 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6230.00 (527963) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POTASH_JCT 6230.00 (527963) 230.0 kV to PECOS 6230.00 (528179) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_005 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_011 | 3PH Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. G24-015-TAP 230.00 (777420) 230.0 kV to YOAKUM 6230.00 (526935) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_012 | 3PH Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_NORTH 6230.00 (527799) 230.0 kV to CUNNIGHM_N 6230.00 (527865) 230.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to CUNINGHAM2 120.000 (527882) 20.0 kV Transmission Circuit #1 b.3. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 b.4. CUNNIGHM_N 6230.00 (527865) 230.0 kV to POTASH_JCT 6230.00 (527963) 230.0 kV Transmission Circuit #1 b.5. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNNIGHM_S 6230.00 (527867) 230.0 kV Transmission Circuit #*1 b.6. CUNNIGHM_N 6230.00 (527865) 230.0 kV to CUNINGHAM3 113.800 (527883) 13.8 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_013 | 3PH Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_006 | 3PH Phase fault on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELK_CT1 345.00 (525850) 345.0 kV to ELK_2 1 18.000 (525845) 18.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 345.00 (525850) 345.0 kV to ELK_1 118.000 (525844) 18.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_014 | 3PH Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDRUNNER 7345.00 (528027) 345.0 kV to ANDREWS 6345.00 (528604) 345.0 kV Transmission Circuit #1 b.2. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #2 b.3. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.4. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.5. PHANTOM 7345.00 (528015) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 b.6. HOBBS_INT 7345.00 (527896) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #2 b.7. RDRUNNER 7345.00 (528027) 345.0 kV to RDRUNNER 3115.00 (528025) 115.0 kV Transmission Circuit #3 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_007 | 3PH Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2020-008345.00 (764980) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7345.00 (523823) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7345.00 (523823) 345.0 kV to GEN-2021-021345.00 (765490) 345.0 kV Transmission Circuit #1 b.4. CARPENTER 7345.00 (523823) 345.0 kV to HARBNGR7 345.00 (531512) 345.0 kV Transmission Circuit #z1 b.5. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_015 | 3PH Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL1 7345.00 (527666) 345.0 kV Transmission Circuit #1 b.2. RSVLT_GEN1 10.6900 (527651) 0.7 kV to RSVLT_WIND1134.500 (527658) 34.5 kV Transmission Circuit #1 b.3. RSVLT_GEN2 10.6900 (527652) 0.7 kV to RSVLT_WIND2134.500 (527659) 34.5 kV Transmission Circuit #1 b.4. RSVLT_WIND1134.500 (527658) 34.5 kV to RSVLT_COL1 134.500 (527660) 34.5 kV Transmission Circuit #1 b.5. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.6. RSVLT_CC_E 7345.00 (527655) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.7. MILO_WIND 10.7000 (527653) 0.7 kV to MILO_CB 34.500 (577120) 34.5 kV Transmission Circuit #1 b.8. MPT3 PRI 34.500 (577121) 34.5 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.9. MILO_WIND 7345.00 (527640) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_CC_E 7345.00 (527655) 345.0 kV Transmission Circuit #1 b.11. RSVLT_CC_W 7345.00 (527654) 345.0 kV to RSVLT_COL2 7345.00 (527667) 345.0 kV Transmission Circuit #1 b.12. RSVLT_WIND2134.500 (527659) 34.5 kV to RSVLT_COL2 134.500 (527661) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_016 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. TOLK 7345.00 (525549) 345.0 kV to G24-043-TAP 345.00 (778260) 345.0 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_017 | 3PH Phase fault on SAGA_SDCOL 7345.00 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7345.00 (527599) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. CROSSROAD 345.00 (527656) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.7. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.8. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.9. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.10. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.11. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.12. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.13. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.14. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.15. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.16. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.17. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.18. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.19. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.20. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_018 | 3PH Phase fault on CROSSROAD 345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROAD 345.00 (527656) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.010.6900 (527615) 0.7 kV Transmission Circuit #1 b.2. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SMEAS 7345.00 (527600) 345.0 kV Transmission Circuit #1 b.3. SAGANCOL2 134.500 (527603) 34.5 kV to SAGSFT4_2.210.6900 (527617) 0.7 kV Transmission Circuit #1 b.4. SAGA_NDCOL 7345.00 (527598) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.5. SAGASCOL1 134.500 (527611) 34.5 kV to SUB BUS #1 34.500 (527628) 34.5 kV Transmission Circuit #1 b.6. GRDXFR4 10.4800 (527606) 0.5 kV to SAGANCOL2 134.500 (527603) 34.5 kV Transmission Circuit #1 b.7. GRDXFR2 10.4800 (527616) 0.5 kV to SAGASCOL2 134.500 (527612) 34.5 kV Transmission Circuit #1 b.8. SAGA_SCOL 7345.00 (527610) 345.0 kV to CROSSROAD 345.00 (527656) 345.0 kV Transmission Circuit #1 b.9. SAGASCOL1 134.500 (527611) 34.5 kV to SAGSFT1_2.210.6900 (527614) 0.7 kV Transmission Circuit #1 b.10. SAGASCOL2 134.500 (527612) 34.5 kV to SUB BUS #2 34.500 (527629) 34.5 kV Transmission Circuit #1 b.11. SAGANCOL2 134.500 (527603) 34.5 kV to SUB BUS #4 134.500 (527609) 34.5 kV Transmission Circuit #1 b.12. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.210.6900 (527607) 0.7 kV Transmission Circuit #1 b.13. GRDXFR1 10.4800 (527613) 0.5 kV to SAGASCOL1 134.500 (527611) 34.5 kV Transmission Circuit #1 b.14. GRDXFR3 10.4800 (527604) 0.5 kV to SAGANCOL1 134.500 (527602) 34.5 kV Transmission Circuit #1 b.15. SAGANCOL1 134.500 (527602) 34.5 kV to SAGSFT3_2.210.6900 (527605) 0.7 kV Transmission Circuit #1 b.16. SAGA_SDCOL 7345.00 (527599) 345.0 kV to SAGA_SCOL 7345.00 (527610) 345.0 kV Transmission Circuit #1 b.17. SAGASCOL2 134.500 (527612) 34.5 kV to SAGSFT2_2.010.6900 (527618) 0.7 kV Transmission Circuit #1 b.18. SAGA_SMEAS 7345.00 (527600) 345.0 kV to SAGA_NCOL 7345.00 (527601) 345.0 kV Transmission Circuit #1 b.19. SAGANCOL1 134.500 (527602) 34.5 kV to SUB BUS #3 134.500 (527608) 34.5 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_019 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_020 | 3PH Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EDDY_CNTY 7345.00 (527802) 345.0 kV to G24-221-TAP 345.00 (782910) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7345.00 (527802) 345.0 kV to KIOWA 7345.00 (527965) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_008 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_009 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_010 | 3PH Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HITCHLAND 7345.00 (523097) 345.0 kV to CARPENTER 7345.00 (523823) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_011 | 3PH Phase fault on GRPLNS-CB2-134.500 (523126) 34 kV Bus a. Apply fault at the GRPLNS-CB2-134.500 (523126) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-WT2-10.5750 (523123) 0.6 kV Transmission Circuit #1 b.2. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-LV4-134.500 (523127) 34.5 kV to GRPLNS-GT4-10.4800 (523133) 0.5 kV Transmission Circuit #1 b.4. GRPLNS-LV2-134.500 (523129) 34.5 kV to GRPLNS-GT2-10.4800 (523132) 0.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-134.500 (523126) 34.5 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3115.00 (523130) 115.0 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-LV4-134.500 (523127) 34.5 kV Transmission Circuit #1 b.8. NBLWND-LV2 134.500 (523128) 34.5 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.9. GRPLNS-CB4-134.500 (523124) 34.5 kV to GRPLNS-WT4-10.5750 (523121) 0.6 kV Transmission Circuit #1 b.10. GRPLNS-HV2-3115.00 (523131) 115.0 kV to GRPLNS-LV2-134.500 (523129) 34.5 kV Transmission Circuit #1 b.11. NOBLE_WND 3115.00 (523103) 115.0 kV to GRPLNS-HV2-3115.00 (523131) 115.0 kV Transmission Circuit #1 b.12. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_021 | 3PH Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KIOWA 7345.00 (527965) 345.0 kV to RDRUNNER 7345.00 (528027) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_012 | 3PH Phase fault on SPNSPUR_WND134.500 (524294) 34 kV Bus a. Apply fault at the SPNSPUR_WND134.500 (524294) 34 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPNSPUR_WND7345.00 (524296) 345.0 kV to SPNSPUR_COL7345.00 (524299) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7345.00 (523961) 345.0 kV to TOLK 7345.00 (525549) 345.0 kV Transmission Circuit #1 b.3. BECKHAM7 345.00 (516059) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #2 b.4. SPNSPUR_GEN10.6900 (524295) 0.7 kV to SPNSPUR_WND134.500 (524294) 34.5 kV Transmission Circuit #1 b.5. POTTER_CO 7345.00 (523961) 345.0 kV to SPNSPUR_WND7345.00 (524296) 345.0 kV Transmission Circuit #1 b.6. HITCHLAND 7345.00 (523097) 345.0 kV to POTTER_CO 7345.00 (523961) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_023 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_024 | 3PH Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM_345 345.00 (526936) 345.0 kV to HOBBS_INT 7345.00 (527896) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 345.00 (526936) 345.0 kV to G20-067-TAP 345.00 (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2021-090345.00 (766120) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 345.00 (526936) 345.0 kV to GEN-2019-011345.00 (763516) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_013 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_014 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_015 | 3PH Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BVRCNTY7 345.00 (515554) 345.0 kV to HITCHLAND 7345.00 (523097) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_025 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT2 118.000 (527902) 18.0 kV Transmission Circuit #1 b.2. HOBBS_INT 3115.00 (527891) 115.0 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_026 | 3PH Phase fault on BENSING 3115.00 (528433) 115 kV Bus a. Apply fault at the BENSING 3115.00 (528433) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to HOBBS_INT 3115.00 (527891) 115.0 kV Transmission Circuit #1 b.3. HIGG 3115.00 (527363) 115.0 kV to BENSING 3115.00 (528433) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_027 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to HOBBS_PLT3 118.000 (527903) 18.0 kV Transmission Circuit #1 b.2. CUNNIGHM_S 6230.00 (527867) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_028 | 3PH Phase fault on INK_BASIN 3115.00 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3115.00 (527027) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. INK_BASIN 3115.00 (527027) 115.0 kV to LE-WAITS 3115.00 (528325) 115.0 kV Transmission Circuit #1 b.2. INK_BASIN 3115.00 (527027) 115.0 kV to ALRDCRTZ_TP3115.00 (527030) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_029 | 3PH Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. YOAKUM 6230.00 (526935) 230.0 kV to INK_BASIN 6230.00 (527028) 230.0 kV Transmission Circuit #1 b.2. INK_BASIN 6230.00 (527028) 230.0 kV to HOBBS_INT 6230.00 (527894) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_030 | 3PH Phase fault on LYNCH_TP 3115.00 (528390) 115 kV Bus a. Apply fault at the LYNCH_TP 3115.00 (528390) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LYNCH_TP 3115.00 (528390) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 b.2. ENRON_TP 3115.00 (528317) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.3. MEDANOS 3115.00 (527954) 115.0 kV to LYNCH_TP 3115.00 (528390) 115.0 kV Transmission Circuit #1 b.4. MADDOX 3115.00 (528355) 115.0 kV to PEARLE 3115.00 (528392) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_016 | 3PH Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_017 | 3PH Phase fault on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6230.00 (523771) 230.0 kV to NICHOLS 6230.00 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3115.00 (523770) 115.0 kV to KIRBY 3115.00 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3115.00 (523748) 115.0 kV to GRAPEVINE 3115.00 (523770) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_031 | 3PH Phase fault on CUNNINHAM 3115.00 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3115.00 (527864) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WARD 3115.00 (528519) 115.0 kV to WHITTEN 3115.00 (528540) 115.0 kV Transmission Circuit #1 b.2. CUNNINHAM 3115.00 (527864) 115.0 kV to MONUMNT_TP 3115.00 (528568) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_018 | 3PH Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. TUCO_INT 6230.00 (525830) 230.0 kV to JONES 6230.00 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 7345.00 (525832) 345.0 kV to ELK_CT1 345.00 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 6230.00 (525830) 230.0 kV to CARLISLE 6230.00 (526161) 230.0 kV Transmission Circuit #1 b.4. O.K.U.2-7 345.00 (511584) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.5. BORDER 7345.00 (515458) 345.0 kV to TUCO_INT 7345.00 (525832) 345.0 kV Transmission Circuit #1 b.6. TUCO_INT 6230.00 (525830) 230.0 kV to HALE_WNDCL16230.00 (525957) 230.0 kV Transmission Circuit #1 b.7. TOLK 6230.00 (525531) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 b.8. SWISHER 6230.00 (525213) 230.0 kV to TUCO_INT 6230.00 (525830) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_019 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_020 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_021 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. COBRN_CREEK3115.00 (523772) 115.0 kV to WHEELER 3115.00 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_032 | 3PH Phase fault on HOBBS_INT 3115.00 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3115.00 (527891) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOBBS_INT 3115.00 (527891) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_033 | 3PH Phase fault on MADDOXG23 3115.00 (528353) 115 kV Bus a. Apply fault at the MADDOXG23 3115.00 (528353) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX 3115.00 (528355) 115.0 kV Transmission Circuit #@1 b.2. MADDOXG23 3115.00 (528353) 115.0 kV to MADDOX_2 113.800 (528362) 13.8 kV Transmission Circuit #1 b.3. MADDOX_3 112.500 (528363) 12.5 kV to MADDOXG23 3115.00 (528353) 115.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_022 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to BUCKNER7 345.00 (531501) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_023 | 3PH Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 345.00 (531449) 345.0 kV to SETAB 7 345.00 (531465) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_035 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_036 | 3PH Phase fault on LEANTL_345 345.00 (528400) 345 kV Bus a. Apply fault at the LEANTL_345 345.00 (528400) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7345.00 (527896) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.3. KIOWA 7345.00 (527965) 345.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #1 b.4. LEA_NATIONL3115.00 (528399) 115.0 kV to LEANTL_345 345.00 (528400) 345.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_037 | 3PH Phase fault on LE-WEST_SUB3115.00 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3115.00 (528333) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #1 b.2. LE-WEST_SUB3115.00 (528333) 115.0 kV to LE-NRTH_INT3115.00 (528334) 115.0 kV Transmission Circuit #1 b.3. LE-WEST_SUB3115.00 (528333) 115.0 kV to G24-261-TAP 115.00 (784800) 115.0 kV Transmission Circuit #1 b.4. ASGI10-010 113.800 (528331) 13.8 kV to LE-WEST_SUB3115.00 (528333) 115.0 kV Transmission Circuit #2 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_024 | 3PH Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7345.00 (523853) 345.0 kV to HOLCOMB7 345.00 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7345.00 (523853) 345.0 kV to G23-015-TAP 345.00 (772280) 345.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_REGIONAL_P4_FAULT_025 | 3PH Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRAPEVINE 6230.00 (523771) 230.0 kV to WHEELER 6230.00 (523777) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6230.00 (523777) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 b.3. DEMPSEYR POI230.00 (511541) 230.0 kV to STLN-DEMARC6230.00 (523779) 230.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR18 PSIS CF | 29W | Transfer Case | GROUP05_LOCAL_P4_FAULT_038 | 3PH Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CROSSROADS 9765.00 (527669) 765.0 kV to PHANTOM 9765.00 (528014) 765.0 kV Transmission Circuit #1 d. Leave Fault on for 16 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 29SP Fault Current 3-Phase (kA) | Request In Service 29SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR18 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 30.0923 | 38.4654 | 8.3731
GEN-2026-PR18 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 29.0525 | 34.4043 | 5.3518
GEN-2026-PR18 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 27.7552 | 32.4737 | 4.7185
GEN-2026-PR18 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 27.7552 | 32.4737 | 4.7185
GEN-2026-PR18 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 21.0863 | 24.8111 | 3.7248
GEN-2026-PR18 | 05 SOUTHWEST | 762442 | G18-004-TAP | 115 | 24.0117 | 27.4019 | 3.3902
GEN-2026-PR18 | 05 SOUTHWEST | 762438 | GEN-2018-004 | 115 | 23.6612 | 26.9444 | 3.2832
GEN-2026-PR18 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 19.1624 | 21.5517 | 2.3893
GEN-2026-PR18 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 19.1624 | 21.5517 | 2.3893
GEN-2026-PR18 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 35.4637 | 36.9599 | 1.4962
GEN-2026-PR18 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 35.4637 | 36.9599 | 1.4962
GEN-2026-PR18 | 05 SOUTHWEST | 528463 | SANGER_SW 3 | 115 | 16.5325 | 17.9982 | 1.4657
GEN-2026-PR18 | 05 SOUTHWEST | 528491 | MONUMENT 3 | 115 | 16.4771 | 17.8625 | 1.3854
GEN-2026-PR18 | 05 SOUTHWEST | 762866 | GEN-2018-052 | 115 | 34.0781 | 35.4573 | 1.3792
GEN-2026-PR18 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 17.8527 | 19.1895 | 1.3368
GEN-2026-PR18 | 05 SOUTHWEST | 528575 | OXYPERMIAN 3 | 115 | 15.8418 | 17.1697 | 1.3279
GEN-2026-PR18 | 05 SOUTHWEST | 528574 | OXY_NHU_RCF3 | 115 | 15.6266 | 16.9127 | 1.2861
GEN-2026-PR18 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 30.2657 | 31.5345 | 1.2688
GEN-2026-PR18 | 05 SOUTHWEST | 528449 | W_BENDER 3 | 115 | 15.282 | 16.5022 | 1.2202
GEN-2026-PR18 | 05 SOUTHWEST | 528317 | ENRON_TP 3 | 115 | 28.8311 | 29.9879 | 1.1568
GEN-2026-PR18 | 05 SOUTHWEST | 528413 | TAYLOR 3 | 115 | 15.0404 | 16.0779 | 1.0375
GEN-2026-PR18 | 05 SOUTHWEST | 528052 | TIPTOP-SOLAR | 115 | 29.495 | 30.5204 | 1.0254
GEN-2026-PR18 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 27.6168 | 28.5145 | 0.8977
GEN-2026-PR18 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.0629 | 12.8808 | 0.8179
GEN-2026-PR18 | 05 SOUTHWEST | 528435 | MILLEN 3 | 115 | 12.0629 | 12.8808 | 0.8179
GEN-2026-PR18 | 05 SOUTHWEST | 528436 | MILLEN_TPE 3 | 115 | 12.0629 | 12.8808 | 0.8179
GEN-2026-PR18 | 05 SOUTHWEST | 528442 | NE_HOBBS 3 | 115 | 12.3581 | 13.1523 | 0.7942
GEN-2026-PR18 | 05 SOUTHWEST | 528470 | E_SANGER 3 | 115 | 13.2097 | 13.9933 | 0.7836
GEN-2026-PR18 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 14.0367 | 14.7472 | 0.7105
GEN-2026-PR18 | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 24.5735 | 25.281 | 0.7075
GEN-2026-PR18 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 24.3372 | 25.0308 | 0.6936
GEN-2026-PR18 | 05 SOUTHWEST | 528498 | W_HOBBS 3 | 115 | 12.64 | 13.3058 | 0.6658
GEN-2026-PR18 | 05 SOUTHWEST | 527845 | C1_MPT_PRI 3 | 115 | 10.5174 | 11.1397 | 0.6223
GEN-2026-PR18 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 20.5659 | 21.1779 | 0.612
GEN-2026-PR18 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 12.8265 | 13.432 | 0.6055
GEN-2026-PR18 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 20.54 | 21.1454 | 0.6054
GEN-2026-PR18 | 05 SOUTHWEST | 528484 | SW_4J44 3 | 115 | 11.9823 | 12.5828 | 0.6005
GEN-2026-PR18 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 13.0771 | 13.6591 | 0.582
GEN-2026-PR18 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 11.0233 | 11.5865 | 0.5632
GEN-2026-PR18 | 05 SOUTHWEST | 527972 | MIDSPRON_TP3 | 115 | 20.1606 | 20.7172 | 0.5566
GEN-2026-PR18 | 05 SOUTHWEST | 528400 | LEANTL_345 | 345 | 11.7995 | 12.3532 | 0.5537
GEN-2026-PR18 | 05 SOUTHWEST | 528456 | N_HOBBS 3 | 115 | 10.4158 | 10.9678 | 0.552
GEN-2026-PR18 | 05 SOUTHWEST | 528480 | OXY_S_HOBBS3 | 115 | 11.2542 | 11.7888 | 0.5346
GEN-2026-PR18 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 25.0568 | 25.5812 | 0.5244
GEN-2026-PR18 | 05 SOUTHWEST | 528020 | BOPCO_PKRLK3 | 115 | 24.412 | 24.9146 | 0.5026
GEN-2026-PR18 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 22.8916 | 23.3662 | 0.4746
GEN-2026-PR18 | 05 SOUTHWEST | 784800 | G24-261-TAP | 115 | 9.9822 | 10.4433 | 0.4611
GEN-2026-PR18 | 05 SOUTHWEST | 784801 | GEN-2024-261 | 115 | 9.9249 | 10.3806 | 0.4557
GEN-2026-PR18 | 05 SOUTHWEST | 784808 | G24-261RC1 | 115 | 9.9249 | 10.3806 | 0.4557
GEN-2026-PR18 | 05 SOUTHWEST | 784809 | G24-261RC2 | 115 | 9.9249 | 10.3806 | 0.4557
GEN-2026-PR18 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 11.1344 | 11.5782 | 0.4438
GEN-2026-PR18 | 05 SOUTHWEST | 528318 | ENRON 3 | 115 | 18.0247 | 18.4676 | 0.4429
GEN-2026-PR18 | 05 SOUTHWEST | 528235 | WOLFCAMP_TP3 | 115 | 22.4502 | 22.8917 | 0.4415
GEN-2026-PR18 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.9088 | 18.3392 | 0.4304
GEN-2026-PR18 | 05 SOUTHWEST | 527000 | GAINES_PLNT7 | 345 | 11.708 | 12.1331 | 0.4251
GEN-2026-PR18 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 15.6868 | 16.1021 | 0.4153
GEN-2026-PR18 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 8.7761 | 9.1796 | 0.4035
GEN-2026-PR18 | 05 SOUTHWEST | 527999 | INTREPDW_TP3 | 115 | 16.4845 | 16.8753 | 0.3908
GEN-2026-PR18 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 16.2991 | 16.6819 | 0.3828
GEN-2026-PR18 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 24.1131 | 24.4773 | 0.3642
GEN-2026-PR18 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 24.1131 | 24.4773 | 0.3642
GEN-2026-PR18 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.0712 | 12.4338 | 0.3626
GEN-2026-PR18 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 12.8559 | 13.2129 | 0.357
GEN-2026-PR18 | 05 SOUTHWEST | 528385 | BUCKEYE 3 | 115 | 8.1416 | 8.4862 | 0.3446
GEN-2026-PR18 | 05 SOUTHWEST | 528603 | NA_ENRICH 3 | 115 | 14.8335 | 15.1719 | 0.3384
GEN-2026-PR18 | 05 SOUTHWEST | 528236 | WOLFCAMP 3 | 115 | 19.5954 | 19.9308 | 0.3354
GEN-2026-PR18 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.9125 | 26.2477 | 0.3352
GEN-2026-PR18 | 05 SOUTHWEST | 527362 | JOHNSON_DRW3 | 115 | 11.7948 | 12.1297 | 0.3349
GEN-2026-PR18 | 05 SOUTHWEST | 528775 | LE-ERF 3 | 115 | 11.7948 | 12.1297 | 0.3349
GEN-2026-PR18 | 05 SOUTHWEST | 528627 | LE-TXACO_TP3 | 115 | 8.0389 | 8.3725 | 0.3336
GEN-2026-PR18 | 05 SOUTHWEST | 785371 | GEN-2024-280 | 345 | 9.4889 | 9.8093 | 0.3204
GEN-2026-PR18 | 05 SOUTHWEST | 527971 | MIDS_PRONTO3 | 115 | 15.3435 | 15.6632 | 0.3197
GEN-2026-PR18 | 05 SOUTHWEST | 527360 | MAPCO 3 | 115 | 11.515 | 11.8336 | 0.3186
GEN-2026-PR18 | 05 SOUTHWEST | 778260 | G24-043-TAP | 345 | 15.9169 | 16.229 | 0.3121
GEN-2026-PR18 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 10.1189 | 10.4286 | 0.3097
GEN-2026-PR18 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.3406 | 8.6498 | 0.3092
GEN-2026-PR18 | 05 SOUTHWEST | 784921 | GEN-2024-265 | 115 | 8.299 | 8.6051 | 0.3061
GEN-2026-PR18 | 05 SOUTHWEST | 784928 | G24-265RC1 | 115 | 8.299 | 8.6051 | 0.3061
GEN-2026-PR18 | 05 SOUTHWEST | 784929 | G24-265RC2 | 115 | 8.299 | 8.6051 | 0.3061
GEN-2026-PR18 | 05 SOUTHWEST | 528581 | BYRD_TP 3 | 115 | 8.693 | 8.9983 | 0.3053
GEN-2026-PR18 | 05 SOUTHWEST | 528392 | PEARLE 3 | 115 | 9.8823 | 10.1869 | 0.3046
GEN-2026-PR18 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.4951 | 9.7962 | 0.3011
GEN-2026-PR18 | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 14.2383 | 14.5372 | 0.2989
GEN-2026-PR18 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 10.606 | 10.8995 | 0.2935
GEN-2026-PR18 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 10.606 | 10.8995 | 0.2935
GEN-2026-PR18 | 05 SOUTHWEST | 528334 | LE-NRTH_INT3 | 115 | 9.4512 | 9.7438 | 0.2926
GEN-2026-PR18 | 05 SOUTHWEST | 787051 | GEN-2024-336 | 230 | 10.6582 | 10.9399 | 0.2817
GEN-2026-PR18 | 05 SOUTHWEST | 528390 | LYNCH_TP 3 | 115 | 10.9249 | 11.2007 | 0.2758
GEN-2026-PR18 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 14.7305 | 15.0038 | 0.2733
GEN-2026-PR18 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 14.7305 | 15.0038 | 0.2733
GEN-2026-PR18 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.7305 | 15.0038 | 0.2733
GEN-2026-PR18 | 05 SOUTHWEST | 528792 | LE-TEXACO 3 | 115 | 7.2252 | 7.4936 | 0.2684
GEN-2026-PR18 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 10.1859 | 10.4534 | 0.2675
GEN-2026-PR18 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.036 | 9.3019 | 0.2659
GEN-2026-PR18 | 05 SOUTHWEST | 528000 | INTREPIDWST3 | 115 | 13.6142 | 13.8791 | 0.2649
GEN-2026-PR18 | 05 SOUTHWEST | 527640 | MILO_WIND 7 | 345 | 14.3273 | 14.592 | 0.2647
GEN-2026-PR18 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.3273 | 14.592 | 0.2647
GEN-2026-PR18 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 16.4571 | 16.7208 | 0.2637
GEN-2026-PR18 | 05 SOUTHWEST | 528341 | LE-SANANDRS3 | 115 | 7.2113 | 7.4747 | 0.2634
GEN-2026-PR18 | 05 SOUTHWEST | 527300 | AM_FRAC 3 | 115 | 10.4539 | 10.7147 | 0.2608
GEN-2026-PR18 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 10.8986 | 11.158 | 0.2594
GEN-2026-PR18 | 05 SOUTHWEST | 528582 | BYRD 3 | 115 | 8.0056 | 8.2635 | 0.2579
GEN-2026-PR18 | 05 SOUTHWEST | 528178 | PECOS 3 | 115 | 13.6341 | 13.8884 | 0.2543
GEN-2026-PR18 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 19.701 | 19.9533 | 0.2523
GEN-2026-PR18 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 19.701 | 19.9533 | 0.2523
GEN-2026-PR18 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 8.2939 | 8.5458 | 0.2519
GEN-2026-PR18 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 13.2639 | 13.5146 | 0.2507
GEN-2026-PR18 | 05 SOUTHWEST | 528422 | DCP_ZIA TP 3 | 115 | 12.2209 | 12.4703 | 0.2494
GEN-2026-PR18 | 05 SOUTHWEST | 766120 | GEN-2021-090 | 345 | 13.1835 | 13.431 | 0.2475
GEN-2026-PR18 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 17.4978 | 17.7384 | 0.2406
GEN-2026-PR18 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.8131 | 14.0536 | 0.2405
GEN-2026-PR18 | 05 SOUTHWEST | 528033 | CPERHEAD_HV3 | 115 | 14.7369 | 14.9774 | 0.2405
GEN-2026-PR18 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 17.3239 | 17.5597 | 0.2358
GEN-2026-PR18 | 05 SOUTHWEST | 786061 | GEN-2024-303 | 345 | 13.2981 | 13.5339 | 0.2358
GEN-2026-PR18 | 05 SOUTHWEST | 786091 | GEN-2024-304 | 345 | 13.2981 | 13.5339 | 0.2358
GEN-2026-PR18 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.7109 | 10.9441 | 0.2332
GEN-2026-PR18 | 05 SOUTHWEST | 778261 | GEN-2024-043 | 345 | 13.6902 | 13.9203 | 0.2301
GEN-2026-PR18 | 05 SOUTHWEST | 528160 | CARLSBAD 3 | 115 | 12.8934 | 13.1218 | 0.2284
GEN-2026-PR18 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 14.5177 | 14.7423 | 0.2246
GEN-2026-PR18 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 13.0984 | 13.3183 | 0.2199
GEN-2026-PR18 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 13.0984 | 13.3183 | 0.2199
GEN-2026-PR18 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 17.0613 | 17.2798 | 0.2185
GEN-2026-PR18 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 15.0404 | 15.2557 | 0.2153
GEN-2026-PR18 | 05 SOUTHWEST | 528396 | XTO_BULLDOG3 | 115 | 11.6978 | 11.9108 | 0.213
GEN-2026-PR18 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 12.1851 | 12.3963 | 0.2112
GEN-2026-PR18 | 05 SOUTHWEST | 528423 | DCP_ZIA 3 | 115 | 11.2026 | 11.4121 | 0.2095
GEN-2026-PR18 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 17.2095 | 17.4146 | 0.2051
GEN-2026-PR18 | 05 SOUTHWEST | 527284 | RUSSELL 3 | 115 | 9.6778 | 9.8817 | 0.2039
GEN-2026-PR18 | 05 SOUTHWEST | 528222 | CHINA_DRAW 3 | 115 | 15.349 | 15.5528 | 0.2038
GEN-2026-PR18 | 05 SOUTHWEST | 528225 | CD_SVC_HV 3 | 115 | 15.349 | 15.5528 | 0.2038
GEN-2026-PR18 | 05 SOUTHWEST | 528420 | ZIA 3 | 115 | 10.9453 | 11.1446 | 0.1993
GEN-2026-PR18 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 21.2151 | 21.4106 | 0.1955
GEN-2026-PR18 | 05 SOUTHWEST | 528533 | DRINKARD_TP3 | 115 | 8.9512 | 9.1466 | 0.1954
GEN-2026-PR18 | 05 SOUTHWEST | 528589 | DRINKARD 3 | 115 | 9.3884 | 9.5806 | 0.1922
GEN-2026-PR18 | 05 SOUTHWEST | 528554 | COOPER_RNCH3 | 115 | 7.3542 | 7.5379 | 0.1837
GEN-2026-PR18 | 05 SOUTHWEST | 528179 | PECOS 6 | 230 | 7.4016 | 7.5789 | 0.1773
GEN-2026-PR18 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 13.0009 | 13.1772 | 0.1763
GEN-2026-PR18 | 05 SOUTHWEST | 527598 | SAGA_NDCOL 7 | 345 | 11.9571 | 12.1305 | 0.1734
GEN-2026-PR18 | 05 SOUTHWEST | 527601 | SAGA_NCOL 7 | 345 | 11.9571 | 12.1305 | 0.1734
GEN-2026-PR18 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 15.6695 | 15.8418 | 0.1723
GEN-2026-PR18 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 11.7495 | 11.9215 | 0.172
GEN-2026-PR18 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 11.7495 | 11.9215 | 0.172
GEN-2026-PR18 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 11.7495 | 11.9215 | 0.172
GEN-2026-PR18 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 15.2299 | 15.4016 | 0.1717
GEN-2026-PR18 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 17.8751 | 18.0452 | 0.1701
GEN-2026-PR18 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 11.218 | 11.3867 | 0.1687
GEN-2026-PR18 | 05 SOUTHWEST | 527080 | EL_PASO 3 | 115 | 17.5872 | 17.7553 | 0.1681
GEN-2026-PR18 | 05 SOUTHWEST | 528151 | FIESTA 3 | 115 | 11.0651 | 11.2326 | 0.1675
GEN-2026-PR18 | 05 SOUTHWEST | 527068 | SHELLC3_TP 3 | 115 | 13.9524 | 14.1198 | 0.1674
GEN-2026-PR18 | 05 SOUTHWEST | 527033 | XTO_CORNEL+3 | 115 | 13.4566 | 13.6228 | 0.1662
GEN-2026-PR18 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.4566 | 13.6228 | 0.1662
GEN-2026-PR18 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 22.0413 | 22.1985 | 0.1572
GEN-2026-PR18 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 5.8153 | 5.972 | 0.1567
GEN-2026-PR18 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.4163 | 9.5712 | 0.1549
GEN-2026-PR18 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.8163 | 7.9704 | 0.1541
GEN-2026-PR18 | 05 SOUTHWEST | 999993 | ZSWSH_999993 | 765 | 7.8163 | 7.9704 | 0.1541
GEN-2026-PR18 | 05 SOUTHWEST | 528540 | WHITTEN 3 | 115 | 10.0632 | 10.2108 | 0.1476
GEN-2026-PR18 | 05 SOUTHWEST | 528622 | LE-SANANDRS2 | 69 | 7.4205 | 7.5673 | 0.1468
GEN-2026-PR18 | 05 SOUTHWEST | 528037 | IMC_#1 3 | 115 | 10.1212 | 10.267 | 0.1458
GEN-2026-PR18 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 7.0566 | 7.2006 | 0.144
GEN-2026-PR18 | 05 SOUTHWEST | 528552 | OIL_CENTER 3 | 115 | 6.9233 | 7.0661 | 0.1428
GEN-2026-PR18 | 05 SOUTHWEST | 782910 | G24-221-TAP | 345 | 9.3159 | 9.458 | 0.1421
GEN-2026-PR18 | 05 SOUTHWEST | 783601 | GEN-2024-221 | 345 | 9.2759 | 9.4167 | 0.1408
GEN-2026-PR18 | 05 SOUTHWEST | 783608 | GEN-2024-C1 | 345 | 9.2759 | 9.4167 | 0.1408
GEN-2026-PR18 | 05 SOUTHWEST | 783609 | GEN-2024-C2 | 345 | 9.2759 | 9.4167 | 0.1408
GEN-2026-PR18 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 32.0643 | 32.2016 | 0.1373
GEN-2026-PR18 | 05 SOUTHWEST | 527024 | ALLRED_SUB 3 | 115 | 11.3884 | 11.5232 | 0.1348
GEN-2026-PR18 | 05 SOUTHWEST | 527322 | GAINES 3 | 115 | 10.5692 | 10.7019 | 0.1327
GEN-2026-PR18 | 05 SOUTHWEST | 527325 | OXY_WSEM_TP3 | 115 | 10.3136 | 10.4457 | 0.1321
GEN-2026-PR18 | 05 SOUTHWEST | 785821 | GEN-2024-295 | 115 | 11.7958 | 11.9273 | 0.1315
GEN-2026-PR18 | 05 SOUTHWEST | 527954 | MEDANOS 3 | 115 | 8.8754 | 9.0044 | 0.129
GEN-2026-PR18 | 05 SOUTHWEST | 528137 | N_CANAL 3 | 115 | 9.736 | 9.8644 | 0.1284
GEN-2026-PR18 | 05 SOUTHWEST | 527805 | OXY_PALINDM3 | 115 | 9.0312 | 9.1587 | 0.1275
GEN-2026-PR18 | 05 SOUTHWEST | 528008 | OXY_ACSR 3 | 115 | 10.9435 | 11.0704 | 0.1269
GEN-2026-PR18 | 05 SOUTHWEST | 528618 | LE-LOVINTON2 | 69 | 8.0615 | 8.1829 | 0.1214
GEN-2026-PR18 | 05 SOUTHWEST | 527074 | SHELLC3 3 | 115 | 11.8976 | 12.018 | 0.1204
GEN-2026-PR18 | 05 SOUTHWEST | 528019 | CHVRN_DUBRV3 | 115 | 10.5224 | 10.6394 | 0.117
GEN-2026-PR18 | 05 SOUTHWEST | 527970 | MAGNUM 3 | 115 | 9.0728 | 9.1881 | 0.1153
GEN-2026-PR18 | 05 SOUTHWEST | 528094 | 7-RIVERS 3 | 115 | 9.182 | 9.2968 | 0.1148
GEN-2026-PR18 | 05 SOUTHWEST | 528512 | EUNICE 3 | 115 | 6.7842 | 6.8956 | 0.1114
GEN-2026-PR18 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.7458 | 14.855 | 0.1092
GEN-2026-PR18 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.6455 | 14.7529 | 0.1074
GEN-2026-PR18 | 05 SOUTHWEST | 528228 | WOOD_DRAW 3 | 115 | 11.273 | 11.3783 | 0.1053
GEN-2026-PR18 | 05 SOUTHWEST | 527022 | APACHE_ROB 3 | 115 | 10.0649 | 10.1697 | 0.1048
GEN-2026-PR18 | 05 SOUTHWEST | 527106 | SAN_ANDRES 3 | 115 | 12.9712 | 13.076 | 0.1048
GEN-2026-PR18 | 05 SOUTHWEST | 527242 | AMERADA 3 | 115 | 12.1884 | 12.2916 | 0.1032
GEN-2026-PR18 | 05 SOUTHWEST | 527961 | POTASH_JCT 2 | 69 | 10.8247 | 10.9252 | 0.1005
GEN-2026-PR18 | 05 SOUTHWEST | 527238 | ROZ 3 | 115 | 12.0196 | 12.1199 | 0.1003
GEN-2026-PR18 | 05 SOUTHWEST | 777420 | G24-015-TAP | 230 | 11.9204 | 12.0189 | 0.0985
GEN-2026-PR18 | 05 SOUTHWEST | 528634 | LE-LEE 2 | 69 | 6.0327 | 6.1293 | 0.0966
GEN-2026-PR18 | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 8.8466 | 8.9423 | 0.0957
GEN-2026-PR18 | 05 SOUTHWEST | 777421 | GEN-2024-015 | 230 | 11.7409 | 11.8364 | 0.0955
GEN-2026-PR18 | 05 SOUTHWEST | 780240 | G24-109-TAP | 345 | 13.2344 | 13.3268 | 0.0924
GEN-2026-PR18 | 05 SOUTHWEST | 528195 | AGAVE_PDURO3 | 115 | 9.7492 | 9.8405 | 0.0913
GEN-2026-PR18 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.9534 | 15.0422 | 0.0888
GEN-2026-PR18 | 05 SOUTHWEST | 528642 | LE-VACUUM 2 | 69 | 5.6664 | 5.7515 | 0.0851
GEN-2026-PR18 | 05 SOUTHWEST | 527711 | EAGLE_CREEK3 | 115 | 7.9708 | 8.0531 | 0.0823
GEN-2026-PR18 | 05 SOUTHWEST | 528134 | SISKO_TP 3 | 115 | 7.8523 | 7.9343 | 0.082
GEN-2026-PR18 | 05 SOUTHWEST | 528194 | MALAGABEND 3 | 115 | 9.4383 | 9.5174 | 0.0791
GEN-2026-PR18 | 05 SOUTHWEST | 528135 | CAVEMAN 3 | 115 | 7.6236 | 7.7021 | 0.0785
GEN-2026-PR18 | 05 SOUTHWEST | 528677 | LE-DSYSRPOI2 | 69 | 6.308 | 6.3856 | 0.0776
GEN-2026-PR18 | 05 SOUTHWEST | 528678 | LE-DSYSOLAR2 | 69 | 6.3015 | 6.3789 | 0.0774
GEN-2026-PR18 | 05 SOUTHWEST | 527821 | CV-DAYTON +3 | 115 | 7.7237 | 7.801 | 0.0773
GEN-2026-PR18 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.7694 | 8.8464 | 0.077
GEN-2026-PR18 | 05 SOUTHWEST | 527021 | CORTEZ 3 | 115 | 8.5857 | 8.6617 | 0.076
GEN-2026-PR18 | 05 SOUTHWEST | 527715 | NAVAJO_2TP 3 | 115 | 7.5881 | 7.6627 | 0.0746
GEN-2026-PR18 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 9.8028 | 9.8769 | 0.0741
GEN-2026-PR18 | 05 SOUTHWEST | 527720 | NAVAJO_3 3 | 115 | 7.5432 | 7.6169 | 0.0737
GEN-2026-PR18 | 05 SOUTHWEST | 527736 | NAVAJO_5TP 3 | 115 | 7.5432 | 7.6169 | 0.0737
GEN-2026-PR18 | 05 SOUTHWEST | 527739 | NAVAJO_4 3 | 115 | 7.5254 | 7.5987 | 0.0733
GEN-2026-PR18 | 05 SOUTHWEST | 527743 | NAVAJO_5 3 | 115 | 7.5277 | 7.601 | 0.0733
GEN-2026-PR18 | 05 SOUTHWEST | 527717 | NAVAJO_2 3 | 115 | 7.4965 | 7.5692 | 0.0727
GEN-2026-PR18 | 05 SOUTHWEST | 528252 | CHVRN_EDDYS3 | 115 | 9.1901 | 9.2624 | 0.0723
GEN-2026-PR18 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.4322 | 24.5028 | 0.0706
GEN-2026-PR18 | 05 SOUTHWEST | 527323 | OXY_WSTSEM 3 | 115 | 7.5392 | 7.6093 | 0.0701
GEN-2026-PR18 | 05 SOUTHWEST | 527941 | CV-MLMAN_TP3 | 115 | 6.8584 | 6.927 | 0.0686
GEN-2026-PR18 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.6154 | 11.6825 | 0.0671
GEN-2026-PR18 | 05 SOUTHWEST | 527929 | PCA 2 | 69 | 8.6034 | 8.6674 | 0.064
GEN-2026-PR18 | 05 SOUTHWEST | 528132 | OCOTILLO 3 | 115 | 6.7942 | 6.8554 | 0.0612
GEN-2026-PR18 | 05 SOUTHWEST | 527056 | ODC 3 | 115 | 10.946 | 11.0056 | 0.0596
GEN-2026-PR18 | 05 SOUTHWEST | 528774 | LE-ERF 2 | 69 | 7.1259 | 7.1833 | 0.0574
GEN-2026-PR18 | 05 SOUTHWEST | 528542 | ZIAHILS13 3 | 115 | 7.6546 | 7.7094 | 0.0548
GEN-2026-PR18 | 05 SOUTHWEST | 528022 | MISSCHEM#2 2 | 69 | 7.9608 | 8.0149 | 0.0541
GEN-2026-PR18 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 9.0235 | 9.0769 | 0.0534
GEN-2026-PR18 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 11.1921 | 11.2441 | 0.052
GEN-2026-PR18 | 05 SOUTHWEST | 786270 | G24-310_311 | 230 | 4.3373 | 4.3855 | 0.0482
GEN-2026-PR18 | 05 SOUTHWEST | 786301 | GEN-2024-311 | 230 | 4.3373 | 4.3855 | 0.0482
GEN-2026-PR18 | 05 SOUTHWEST | 528679 | LE-TATMGOAB2 | 69 | 5.4624 | 5.5105 | 0.0481
GEN-2026-PR18 | 05 SOUTHWEST | 786271 | GEN-2024-310 | 230 | 4.3268 | 4.3748 | 0.048
GEN-2026-PR18 | 05 SOUTHWEST | 527984 | CHVRN_DAGL+3 | 115 | 5.5165 | 5.5644 | 0.0479
GEN-2026-PR18 | 05 SOUTHWEST | 527942 | CV-MILLMAN 3 | 115 | 5.5948 | 5.6404 | 0.0456
GEN-2026-PR18 | 05 SOUTHWEST | 527778 | ARTESIA_CC 3 | 115 | 5.8585 | 5.9028 | 0.0443
GEN-2026-PR18 | 05 SOUTHWEST | 527809 | CV-8_MILE 3 | 115 | 5.8577 | 5.9013 | 0.0436
GEN-2026-PR18 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 24.9845 | 25.0275 | 0.043
GEN-2026-PR18 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 24.9845 | 25.0275 | 0.043
GEN-2026-PR18 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 24.7687 | 24.8109 | 0.0422
GEN-2026-PR18 | 05 SOUTHWEST | 527985 | CHVRN_DAGLK3 | 115 | 5.186 | 5.2282 | 0.0422
GEN-2026-PR18 | 05 SOUTHWEST | 527980 | DUVAL_#1 2 | 69 | 6.6919 | 6.7297 | 0.0378
GEN-2026-PR18 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7894 | 11.8267 | 0.0373
GEN-2026-PR18 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 6.8748 | 6.9108 | 0.036
GEN-2026-PR18 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.7588 | 9.7944 | 0.0356
GEN-2026-PR18 | 05 SOUTHWEST | 528768 | LE-ANCELL 2 | 69 | 5.6335 | 5.6691 | 0.0356
GEN-2026-PR18 | 05 SOUTHWEST | 527455 | RSWL_SLRCOL3 | 115 | 6.7989 | 6.8341 | 0.0352
GEN-2026-PR18 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.4068 | 10.4419 | 0.0351
GEN-2026-PR18 | 05 SOUTHWEST | 528671 | LE-S_LOVITN2 | 69 | 4.0303 | 4.0652 | 0.0349
GEN-2026-PR18 | 05 SOUTHWEST | 764935 | GEN-2020-067 | 345 | 7.3924 | 7.4268 | 0.0344
GEN-2026-PR18 | 05 SOUTHWEST | 527470 | CHVS_SLRCOL3 | 115 | 6.6532 | 6.6869 | 0.0337
GEN-2026-PR18 | 05 SOUTHWEST | 527125 | DENVER_CTY 2 | 69 | 9.2711 | 9.3035 | 0.0324
GEN-2026-PR18 | 05 SOUTHWEST | 527948 | CV-LUSK_TP 3 | 115 | 4.6948 | 4.7269 | 0.0321
GEN-2026-PR18 | 05 SOUTHWEST | 528076 | CV-WALTCYN 3 | 115 | 4.8981 | 4.9302 | 0.0321
GEN-2026-PR18 | 05 SOUTHWEST | 775721 | ASG-2023-001 | 115 | 6.0553 | 6.0867 | 0.0314
GEN-2026-PR18 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 16.1882 | 16.2193 | 0.0311
GEN-2026-PR18 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 16.0464 | 16.0768 | 0.0304
GEN-2026-PR18 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 16.0158 | 16.0462 | 0.0304
GEN-2026-PR18 | 05 SOUTHWEST | 766031 | A21-001-TAP | 69 | 3.8133 | 3.8436 | 0.0303
GEN-2026-PR18 | 05 SOUTHWEST | 527678 | SMITH 2 | 69 | 6.2352 | 6.2654 | 0.0302
GEN-2026-PR18 | 05 SOUTHWEST | 527710 | EAGLE_CREEK2 | 69 | 6.2466 | 6.2768 | 0.0302
GEN-2026-PR18 | 05 SOUTHWEST | 766030 | ASGI-2021-01 | 69 | 3.8013 | 3.8314 | 0.0301
GEN-2026-PR18 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4754 | 4.5044 | 0.029
GEN-2026-PR18 | 05 SOUTHWEST | 526943 | LG-PLAINS +3 | 115 | 8.6945 | 8.7233 | 0.0288
GEN-2026-PR18 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 8.6779 | 8.7066 | 0.0287
GEN-2026-PR18 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1838 | 11.212 | 0.0282
GEN-2026-PR18 | 05 SOUTHWEST | 528406 | MALJMAR1&2 3 | 115 | 4.1359 | 4.1635 | 0.0276
GEN-2026-PR18 | 05 SOUTHWEST | 527193 | LG-PLSHILL+3 | 115 | 8.4737 | 8.501 | 0.0273
GEN-2026-PR18 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.4573 | 8.4845 | 0.0272
GEN-2026-PR18 | 05 SOUTHWEST | 528253 | CHVRN_JMPSP3 | 115 | 5.594 | 5.6206 | 0.0266
GEN-2026-PR18 | 05 SOUTHWEST | 527370 | TENNECO_TAP2 | 69 | 6.1201 | 6.1462 | 0.0261
GEN-2026-PR18 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5756 | 11.6016 | 0.026
GEN-2026-PR18 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5756 | 11.6016 | 0.026
GEN-2026-PR18 | 05 SOUTHWEST | 527533 | SW4J795_E 3 | 115 | 5.6919 | 5.7177 | 0.0258
GEN-2026-PR18 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.5023 | 11.528 | 0.0257
GEN-2026-PR18 | 05 SOUTHWEST | 527529 | RIACBRSH_TP3 | 115 | 5.5254 | 5.5497 | 0.0243
GEN-2026-PR18 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.3842 | 14.4082 | 0.024
GEN-2026-PR18 | 05 SOUTHWEST | 528699 | LE-GRAY 2 | 69 | 3.6391 | 3.663 | 0.0239
GEN-2026-PR18 | 05 SOUTHWEST | 527597 | TWEEDY 3 | 115 | 5.3624 | 5.3859 | 0.0235
GEN-2026-PR18 | 05 SOUTHWEST | 528675 | LE-FAMARISS2 | 69 | 3.6085 | 3.632 | 0.0235
GEN-2026-PR18 | 05 SOUTHWEST | 527536 | BRASHER 3 | 115 | 5.2997 | 5.3221 | 0.0224
GEN-2026-PR18 | 05 SOUTHWEST | 527733 | NAVAJO_1 2 | 69 | 5.3218 | 5.3437 | 0.0219
GEN-2026-PR18 | 05 SOUTHWEST | 527947 | CV-LUSK 3 | 115 | 3.8343 | 3.8557 | 0.0214
GEN-2026-PR18 | 05 SOUTHWEST | 527757 | ARTESIA_TP 2 | 69 | 5.2152 | 5.2362 | 0.021
GEN-2026-PR18 | 05 SOUTHWEST | 780241 | GEN-2024-109 | 345 | 6.5791 | 6.5998 | 0.0207
GEN-2026-PR18 | 05 SOUTHWEST | 527747 | ARTESIA_TWN2 | 69 | 5.1306 | 5.1509 | 0.0203
GEN-2026-PR18 | 05 SOUTHWEST | 527371 | TENNECO 2 | 69 | 5.3838 | 5.4038 | 0.02
GEN-2026-PR18 | 05 SOUTHWEST | 528029 | IMC_#2 2 | 69 | 4.8153 | 4.8349 | 0.0196
GEN-2026-PR18 | 05 SOUTHWEST | 527553 | SIERRA 3 | 115 | 4.9188 | 4.938 | 0.0192
GEN-2026-PR18 | 05 SOUTHWEST | 528159 | CARLSBAD 2 | 69 | 4.7494 | 4.7679 | 0.0185
GEN-2026-PR18 | 05 SOUTHWEST | 527935 | CV-SKELLY 3 | 115 | 3.5562 | 3.5746 | 0.0184
GEN-2026-PR18 | 05 SOUTHWEST | 527508 | PRICE 3 | 115 | 4.8415 | 4.8595 | 0.018
GEN-2026-PR18 | 05 SOUTHWEST | 528043 | UNITEDSALT 2 | 69 | 4.6056 | 4.6236 | 0.018
GEN-2026-PR18 | 05 SOUTHWEST | 527822 | CV-TURKYTRK3 | 115 | 3.6926 | 3.7098 | 0.0172
GEN-2026-PR18 | 05 SOUTHWEST | 767221 | GEN-2022-012 | 345 | 22.3212 | 22.3384 | 0.0172
GEN-2026-PR18 | 05 SOUTHWEST | 767301 | GEN-2022-016 | 345 | 22.3212 | 22.3384 | 0.0172
GEN-2026-PR18 | 05 SOUTHWEST | 528079 | CV-CONEBUTE3 | 115 | 3.5782 | 3.5953 | 0.0171
GEN-2026-PR18 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.7973 | 9.8141 | 0.0168
GEN-2026-PR18 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 7.217 | 7.2338 | 0.0168
GEN-2026-PR18 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.7973 | 9.8141 | 0.0168
GEN-2026-PR18 | 05 SOUTHWEST | 767321 | GEN-2022-017 | 345 | 21.9795 | 21.9962 | 0.0167
GEN-2026-PR18 | 05 SOUTHWEST | 527099 | DC_EAST 2 | 69 | 6.4974 | 6.5125 | 0.0151
GEN-2026-PR18 | 05 SOUTHWEST | 527111 | WASSON 2 | 69 | 6.3569 | 6.3716 | 0.0147
GEN-2026-PR18 | 05 SOUTHWEST | 528617 | LE-WAITS 2 | 69 | 3.7204 | 3.7348 | 0.0144
GEN-2026-PR18 | 05 SOUTHWEST | 527938 | CV-MALJAMAR3 | 115 | 3.1304 | 3.1447 | 0.0143
GEN-2026-PR18 | 05 SOUTHWEST | 528776 | LE-GAINES 2 | 69 | 3.5684 | 3.5824 | 0.014
GEN-2026-PR18 | 05 SOUTHWEST | 527258 | ALG-SOLAR | 115 | 7.0553 | 7.0688 | 0.0135
GEN-2026-PR18 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.8574 | 8.8709 | 0.0135
GEN-2026-PR18 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 19.6404 | 19.6538 | 0.0134
GEN-2026-PR18 | 05 SOUTHWEST | 527262 | SULPHUR 3 | 115 | 6.9858 | 6.9991 | 0.0133
GEN-2026-PR18 | 05 SOUTHWEST | 527754 | CV-ARTESIA 2 | 69 | 4.1537 | 4.1669 | 0.0132
GEN-2026-PR18 | 05 SOUTHWEST | 528703 | LE-DENTN_TP2 | 69 | 2.7234 | 2.7364 | 0.013
GEN-2026-PR18 | 05 SOUTHWEST | 528714 | LE-FORT_SW 2 | 69 | 3.4962 | 3.5089 | 0.0127
GEN-2026-PR18 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 6.743 | 6.7553 | 0.0123
GEN-2026-PR18 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 6.743 | 6.7553 | 0.0123
GEN-2026-PR18 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3792 | 6.3915 | 0.0123
GEN-2026-PR18 | 05 SOUTHWEST | 527811 | CV-KEWAN_TP3 | 115 | 3.1253 | 3.1376 | 0.0123
GEN-2026-PR18 | 05 SOUTHWEST | 524885 | SN_JUAN_SS 6 | 230 | 4.6812 | 4.6928 | 0.0116
GEN-2026-PR18 | 05 SOUTHWEST | 527345 | LEGACY 2 | 69 | 4.2199 | 4.2312 | 0.0113
GEN-2026-PR18 | 05 SOUTHWEST | 525516 | XS1_MPT1PRI3 | 115 | 14.3794 | 14.3905 | 0.0111
GEN-2026-PR18 | 05 SOUTHWEST | 527812 | CV-KEWANEE 3 | 115 | 2.9729 | 2.984 | 0.0111
GEN-2026-PR18 | 05 SOUTHWEST | 515378 | WWRDEHV9 | 765 | 5.8205 | 5.8314 | 0.0109
GEN-2026-PR18 | 05 SOUTHWEST | 527815 | CV-HENSH_TP3 | 115 | 2.9253 | 2.9361 | 0.0108
GEN-2026-PR18 | 05 SOUTHWEST | 527339 | DOSS 2 | 69 | 4.4742 | 4.4849 | 0.0107
GEN-2026-PR18 | 05 SOUTHWEST | 527664 | CV-CTTNWD +2 | 69 | 3.7325 | 3.7432 | 0.0107
GEN-2026-PR18 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.4499 | 4.4601 | 0.0102
GEN-2026-PR18 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.3317 | 11.3419 | 0.0102
GEN-2026-PR18 | 05 SOUTHWEST | 528707 | LE-DENTON 2 | 69 | 2.4005 | 2.4105 | 0.01
GEN-2026-PR18 | 05 SOUTHWEST | 527932 | CV-LOCO_TP 3 | 115 | 2.6691 | 2.678 | 0.0089
GEN-2026-PR18 | 05 SOUTHWEST | 528046 | STRATA 2 | 69 | 3.2573 | 3.2662 | 0.0089
GEN-2026-PR18 | 05 SOUTHWEST | 528062 | IMC_#3 2 | 69 | 3.2334 | 3.2422 | 0.0088
GEN-2026-PR18 | 05 SOUTHWEST | 528650 | LE-SAUNDERS2 | 69 | 2.0829 | 2.0917 | 0.0088
GEN-2026-PR18 | 05 SOUTHWEST | 527996 | KERMAC 2 | 69 | 3.2595 | 3.2682 | 0.0087
GEN-2026-PR18 | 05 SOUTHWEST | 527563 | ROSWLL_INT 2 | 69 | 4.2331 | 4.2417 | 0.0086
GEN-2026-PR18 | 05 SOUTHWEST | 528687 | LE-PRAIRIVW2 | 69 | 2.6678 | 2.6762 | 0.0084
GEN-2026-PR18 | 05 SOUTHWEST | 523040 | OLYMPIA7 | 345 | 14.3514 | 14.3596 | 0.0082
GEN-2026-PR18 | 05 SOUTHWEST | 527671 | COTTONWOOD 2 | 69 | 3.2752 | 3.2834 | 0.0082
GEN-2026-PR18 | 05 SOUTHWEST | 528644 | LE-BAYWAWND2 | 69 | 2.0626 | 2.0708 | 0.0082
GEN-2026-PR18 | 05 SOUTHWEST | 528645 | LE-BAYWAPOI2 | 69 | 2.0632 | 2.0714 | 0.0082
GEN-2026-PR18 | 05 SOUTHWEST | 778200 | G24-041-TAP | 345 | 9.4723 | 9.4805 | 0.0082
GEN-2026-PR18 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.5463 | 11.5544 | 0.0081
GEN-2026-PR18 | 05 SOUTHWEST | 528646 | LE-ANDERSON2 | 69 | 2.0533 | 2.0614 | 0.0081
GEN-2026-PR18 | 05 SOUTHWEST | 527096 | OXY_DC_WST 2 | 69 | 4.7768 | 4.7848 | 0.008
GEN-2026-PR18 | 05 SOUTHWEST | 527183 | JAYBEE 2 | 69 | 4.6319 | 4.6398 | 0.0079
GEN-2026-PR18 | 05 SOUTHWEST | 527201 | SEAGRAVES 2 | 69 | 5.8502 | 5.8581 | 0.0079
GEN-2026-PR18 | 05 SOUTHWEST | 528718 | LE-NEWTEX 2 | 69 | 2.7513 | 2.7591 | 0.0078
GEN-2026-PR18 | 05 SOUTHWEST | 526735 | TERRY_CNTY 2 | 69 | 7.3784 | 7.386 | 0.0076
GEN-2026-PR18 | 05 SOUTHWEST | 527217 | MOSS 2 | 69 | 5.74 | 5.7476 | 0.0076
GEN-2026-PR18 | 05 SOUTHWEST | 528190 | S_LOVING_TP2 | 69 | 3.0032 | 3.0106 | 0.0074
GEN-2026-PR18 | 05 SOUTHWEST | 528747 | LE-ALLRED 2 | 69 | 4.4153 | 4.4227 | 0.0074
GEN-2026-PR18 | 05 SOUTHWEST | 527093 | SW_7848 2 | 69 | 4.4791 | 4.486 | 0.0069
GEN-2026-PR18 | 05 SOUTHWEST | 527575 | SW_4702 2 | 69 | 3.7816 | 3.7884 | 0.0068
GEN-2026-PR18 | 05 SOUTHWEST | 527989 | NMPOTASH 2 | 69 | 2.7842 | 2.7905 | 0.0063
GEN-2026-PR18 | 05 SOUTHWEST | 528759 | LE-TP51 2 | 69 | 2.4241 | 2.4302 | 0.0061
GEN-2026-PR18 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 13.2234 | 13.2294 | 0.006
GEN-2026-PR18 | 05 SOUTHWEST | 528050 | DUVAL_#3 2 | 69 | 2.665 | 2.6709 | 0.0059
GEN-2026-PR18 | 05 SOUTHWEST | 525521 | EASTER_WND 6 | 230 | 8.0836 | 8.0893 | 0.0057
GEN-2026-PR18 | 05 SOUTHWEST | 527189 | LG-SEAGRAVE2 | 69 | 3.9582 | 3.9639 | 0.0057
GEN-2026-PR18 | 05 SOUTHWEST | 527657 | CV-LAKARTHR2 | 69 | 2.7038 | 2.7094 | 0.0056
GEN-2026-PR18 | 05 SOUTHWEST | 528197 | CB_WTRFLDTP2 | 69 | 2.6512 | 2.6568 | 0.0056
GEN-2026-PR18 | 05 SOUTHWEST | 528655 | LE-WILAM_TP2 | 69 | 1.6425 | 1.648 | 0.0055
GEN-2026-PR18 | 05 SOUTHWEST | 523041 | FRWLN7 | 345 | 11.7032 | 11.7086 | 0.0054
GEN-2026-PR18 | 05 SOUTHWEST | 528093 | 7-RIVERS 2 | 69 | 2.5379 | 2.5431 | 0.0052
GEN-2026-PR18 | 05 SOUTHWEST | 778201 | GEN-2024-041 | 345 | 7.507 | 7.5122 | 0.0052
GEN-2026-PR18 | 05 SOUTHWEST | 778238 | GEN-2024-042 | 345 | 7.507 | 7.5122 | 0.0052
GEN-2026-PR18 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 9.9849 | 9.99 | 0.0051
GEN-2026-PR18 | 05 SOUTHWEST | 526352 | LEHMAN 3 | 115 | 5.1403 | 5.1454 | 0.0051
GEN-2026-PR18 | 05 SOUTHWEST | 527350 | XTO_ROBRTSN2 | 69 | 2.8327 | 2.8377 | 0.005
GEN-2026-PR18 | 05 SOUTHWEST | 527785 | ATOKA 2 | 69 | 2.5072 | 2.5121 | 0.0049
GEN-2026-PR18 | 05 SOUTHWEST | 515951 | PERSIMN7 | 345 | 11.5485 | 11.5531 | 0.0046
GEN-2026-PR18 | 05 SOUTHWEST | 528780 | LE-NITROTEC2 | 69 | 2.1208 | 2.1254 | 0.0046
GEN-2026-PR18 | 05 SOUTHWEST | 528754 | LE-HIGGBTHM2 | 69 | 2.1025 | 2.107 | 0.0045
GEN-2026-PR18 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.6369 | 5.6413 | 0.0044
GEN-2026-PR18 | 05 SOUTHWEST | 527013 | PHIL_PMP_TP2 | 69 | 3.5708 | 3.5752 | 0.0044
GEN-2026-PR18 | 05 SOUTHWEST | 528056 | IMC_#4 2 | 69 | 2.2706 | 2.2749 | 0.0043
GEN-2026-PR18 | 05 SOUTHWEST | 523019 | OSLO-SYLVIE7 | 345 | 10.6283 | 10.6324 | 0.0041
GEN-2026-PR18 | 05 SOUTHWEST | 523020 | SYLVIE 7 | 345 | 10.6283 | 10.6324 | 0.0041
GEN-2026-PR18 | 05 SOUTHWEST | 523030 | OLSO 7 | 345 | 10.6283 | 10.6324 | 0.0041
GEN-2026-PR18 | 05 SOUTHWEST | 527117 | SW_7814 2 | 69 | 3.3119 | 3.3157 | 0.0038
GEN-2026-PR18 | 05 SOUTHWEST | 527355 | BOARDMAN 2 | 69 | 2.5003 | 2.5041 | 0.0038
GEN-2026-PR18 | 05 SOUTHWEST | 562020 | PRSCRKII 7 | 345 | 10.5465 | 10.5503 | 0.0038
GEN-2026-PR18 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.6235 | 6.6273 | 0.0038
GEN-2026-PR18 | 05 SOUTHWEST | 526506 | LG-DOCWEBR 2 | 69 | 5.2228 | 5.2265 | 0.0037
GEN-2026-PR18 | 05 SOUTHWEST | 527212 | DIAMONDBACK3 | 115 | 3.649 | 3.6526 | 0.0036
GEN-2026-PR18 | 05 SOUTHWEST | 526971 | TOKIO_TP 2 | 69 | 3.9021 | 3.9056 | 0.0035
GEN-2026-PR18 | 05 SOUTHWEST | 527772 | ARTSA_SR_TP2 | 69 | 2.1122 | 2.1157 | 0.0035
GEN-2026-PR18 | 05 SOUTHWEST | 528215 | NAVAMAL_TP 2 | 69 | 2.0719 | 2.0752 | 0.0033
GEN-2026-PR18 | 05 SOUTHWEST | 528659 | LE-WILLIAMS2 | 69 | 1.281 | 1.2843 | 0.0033
GEN-2026-PR18 | 05 SOUTHWEST | 528763 | LE-TP91 2 | 69 | 1.8046 | 1.8079 | 0.0033
GEN-2026-PR18 | 05 SOUTHWEST | 527762 | ARTSA_CC_TP2 | 69 | 2.0388 | 2.042 | 0.0032
GEN-2026-PR18 | 05 SOUTHWEST | 527775 | ARTESIA_SR 2 | 69 | 2.0328 | 2.036 | 0.0032
GEN-2026-PR18 | 05 SOUTHWEST | 515825 | GRTWSRN7 | 345 | 9.3731 | 9.3761 | 0.003
GEN-2026-PR18 | 05 SOUTHWEST | 527514 | CV-PINE 2 | 69 | 2.5353 | 2.5383 | 0.003
GEN-2026-PR18 | 05 SOUTHWEST | 528663 | LE-DALLAS 2 | 69 | 1.2266 | 1.2296 | 0.003
GEN-2026-PR18 | 05 SOUTHWEST | 528204 | CB_WTRFIELD2 | 69 | 1.9039 | 1.9068 | 0.0029
GEN-2026-PR18 | 05 SOUTHWEST | 527761 | ARTESIA_W 2 | 69 | 1.9086 | 1.9114 | 0.0028
GEN-2026-PR18 | 05 SOUTHWEST | 527768 | ARTESIA_CC 2 | 69 | 1.8558 | 1.8585 | 0.0027
GEN-2026-PR18 | 05 SOUTHWEST | 527650 | CV-HAGERMAN2 | 69 | 1.8584 | 1.861 | 0.0026
GEN-2026-PR18 | 05 SOUTHWEST | 528217 | NAVAJOMALGA2 | 69 | 1.8164 | 1.8189 | 0.0025
GEN-2026-PR18 | 05 SOUTHWEST | 527589 | CV-ORCHARD 2 | 69 | 2.2585 | 2.2609 | 0.0024
GEN-2026-PR18 | 05 SOUTHWEST | 528003 | CV-DAGGR&IH2 | 69 | 1.73 | 1.7324 | 0.0024
GEN-2026-PR18 | 05 SOUTHWEST | 526993 | LG-WELLMAN 2 | 69 | 3.2735 | 3.2758 | 0.0023
GEN-2026-PR18 | 05 SOUTHWEST | 527261 | SULPHUR 2 | 69 | 3.7176 | 3.7199 | 0.0023
GEN-2026-PR18 | 05 SOUTHWEST | 527365 | FLANNAGAN 2 | 69 | 1.9498 | 1.9521 | 0.0023
GEN-2026-PR18 | 05 SOUTHWEST | 527377 | LG-FLOREYTP2 | 69 | 1.9498 | 1.9521 | 0.0023
GEN-2026-PR18 | 05 SOUTHWEST | 527763 | CV-W_ARTSIA2 | 69 | 1.7131 | 1.7154 | 0.0023
GEN-2026-PR18 | 05 SOUTHWEST | 527213 | LG-TH&WELCH3 | 115 | 2.8486 | 2.8508 | 0.0022
GEN-2026-PR18 | 05 SOUTHWEST | 526499 | LG-MEADOWTP2 | 69 | 3.913 | 3.915 | 0.002
GEN-2026-PR18 | 05 SOUTHWEST | 526985 | WELLMAN 2 | 69 | 3.0473 | 3.0493 | 0.002
GEN-2026-PR18 | 05 SOUTHWEST | 527376 | LG-FLOREY+ 2 | 69 | 1.7921 | 1.794 | 0.0019
GEN-2026-PR18 | 05 SOUTHWEST | 528665 | LE-CAPROCK 2 | 69 | 0.9809 | 0.9828 | 0.0019
GEN-2026-PR18 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 6.1557 | 6.1575 | 0.0018
GEN-2026-PR18 | 05 SOUTHWEST | 526747 | LG-BROWNFLD2 | 69 | 3.7593 | 3.7611 | 0.0018
GEN-2026-PR18 | 05 SOUTHWEST | 528784 | LE-DARBY 2 | 69 | 1.3161 | 1.3179 | 0.0018
GEN-2026-PR18 | 05 SOUTHWEST | 527223 | LG-MC&SMNL+2 | 69 | 2.7539 | 2.7556 | 0.0017
GEN-2026-PR18 | 05 SOUTHWEST | 527619 | DEXTER_TP 2 | 69 | 1.913 | 1.9147 | 0.0017
GEN-2026-PR18 | 05 SOUTHWEST | 585420 | SUBST HS | 345 | 7.1309 | 7.1326 | 0.0017
GEN-2026-PR18 | 05 SOUTHWEST | 527007 | PHIL_PMP 2 | 69 | 2.21 | 2.2116 | 0.0016
GEN-2026-PR18 | 05 SOUTHWEST | 527211 | DIAMONDBACK2 | 69 | 3.0761 | 3.0777 | 0.0016
GEN-2026-PR18 | 05 SOUTHWEST | 527215 | LG-WELCH 3 | 115 | 2.4592 | 2.4608 | 0.0016
GEN-2026-PR18 | 05 SOUTHWEST | 526416 | SLAUGTER_TP2 | 69 | 3.3118 | 3.3133 | 0.0015
GEN-2026-PR18 | 05 SOUTHWEST | 526965 | KINNEY 2 | 69 | 2.5697 | 2.5712 | 0.0015
GEN-2026-PR18 | 05 SOUTHWEST | 527626 | CV-DEXTER 2 | 69 | 1.7489 | 1.7504 | 0.0015
GEN-2026-PR18 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.3062 | 8.3076 | 0.0014
GEN-2026-PR18 | 05 SOUTHWEST | 527214 | LG-THUNDRHD3 | 115 | 2.2791 | 2.2805 | 0.0014
GEN-2026-PR18 | 05 SOUTHWEST | 527253 | ADAIR 2 | 69 | 2.8626 | 2.864 | 0.0014
GEN-2026-PR18 | 05 SOUTHWEST | 527271 | LG-FOSTERTP2 | 69 | 2.9672 | 2.9686 | 0.0014
GEN-2026-PR18 | 05 SOUTHWEST | 527685 | CV-YO_TP 2 | 69 | 1.7554 | 1.7568 | 0.0014
GEN-2026-PR18 | 05 SOUTHWEST | 526754 | BROWNFIELD 2 | 69 | 3.2157 | 3.217 | 0.0013
GEN-2026-PR18 | 05 SOUTHWEST | 527229 | OZRK_MAH02 2 | 69 | 2.8719 | 2.8732 | 0.0013
GEN-2026-PR18 | 05 SOUTHWEST | 528211 | WHITES_CTY 2 | 69 | 1.343 | 1.3443 | 0.0013
GEN-2026-PR18 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.1664 | 10.1676 | 0.0012
GEN-2026-PR18 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.1517 | 5.1529 | 0.0012
GEN-2026-PR18 | 05 SOUTHWEST | 526761 | BROWNFLD_TP2 | 69 | 2.978 | 2.9792 | 0.0012
GEN-2026-PR18 | 05 SOUTHWEST | 527247 | CEDARLAKE 2 | 69 | 2.6721 | 2.6733 | 0.0012
GEN-2026-PR18 | 05 SOUTHWEST | 527250 | OXY_CEDRLKE2 | 69 | 2.6807 | 2.6819 | 0.0012
GEN-2026-PR18 | 05 SOUTHWEST | 527633 | DEXTER 2 | 69 | 1.6108 | 1.612 | 0.0012
GEN-2026-PR18 | 05 SOUTHWEST | 522892 | MU-BROWNFLD2 | 69 | 2.8811 | 2.8822 | 0.0011
GEN-2026-PR18 | 05 SOUTHWEST | 525649 | LC-LTTLFLD 2 | 69 | 4.8298 | 4.8309 | 0.0011
GEN-2026-PR18 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.8198 | 4.8209 | 0.0011
GEN-2026-PR18 | 05 SOUTHWEST | 526999 | UNION_TX 2 | 69 | 2.5944 | 2.5955 | 0.0011
GEN-2026-PR18 | 05 SOUTHWEST | 523131 | GRPLNS-HV2-3 | 115 | 9.323 | 9.324 | 0.001
GEN-2026-PR18 | 05 SOUTHWEST | 527270 | LG-FOSTER+ 2 | 69 | 2.5408 | 2.5418 | 0.001
GEN-2026-PR18 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.3626 | 4.3635 | 0.0009
GEN-2026-PR18 | 05 SOUTHWEST | 526711 | LG-DIXON 2 | 69 | 2.6343 | 2.6352 | 0.0009
GEN-2026-PR18 | 05 SOUTHWEST | 527235 | LG-ASHMORE 2 | 69 | 2.3938 | 2.3947 | 0.0009
GEN-2026-PR18 | 05 SOUTHWEST | 527305 | LG-SAWYERFL2 | 69 | 2.2674 | 2.2683 | 0.0009
GEN-2026-PR18 | 05 SOUTHWEST | 527692 | CV-YO 2 | 69 | 1.4231 | 1.424 | 0.0009
GEN-2026-PR18 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.2947 | 4.2955 | 0.0008
GEN-2026-PR18 | 05 SOUTHWEST | 526777 | GOODPASTURE2 | 69 | 2.5323 | 2.5331 | 0.0008
GEN-2026-PR18 | 05 SOUTHWEST | 526409 | SLAUGHTER 2 | 69 | 2.3402 | 2.3409 | 0.0007
GEN-2026-PR18 | 05 SOUTHWEST | 527224 | LG-SEMINOLE2 | 69 | 1.7845 | 1.7852 | 0.0007
GEN-2026-PR18 | 05 SOUTHWEST | 523130 | GRPLNS-HV4-3 | 115 | 6.993 | 6.9936 | 0.0006
GEN-2026-PR18 | 05 SOUTHWEST | 525671 | BAINER 2 | 69 | 3.6673 | 3.6679 | 0.0006
GEN-2026-PR18 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.5972 | 3.5978 | 0.0006
GEN-2026-PR18 | 05 SOUTHWEST | 526953 | TOKIO 2 | 69 | 1.6867 | 1.6873 | 0.0006
GEN-2026-PR18 | 05 SOUTHWEST | 526959 | LG-TOKIO 2 | 69 | 1.6797 | 1.6803 | 0.0006
GEN-2026-PR18 | 05 SOUTHWEST | 526979 | LG-JS_SMITH2 | 69 | 2.2109 | 2.2115 | 0.0006
GEN-2026-PR18 | 05 SOUTHWEST | 525612 | W_LITTLFLD+2 | 69 | 3.1073 | 3.1078 | 0.0005
GEN-2026-PR18 | 05 SOUTHWEST | 525697 | PUMP/YH_TP 2 | 69 | 3.3302 | 3.3307 | 0.0005
GEN-2026-PR18 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.9059 | 4.9064 | 0.0005
GEN-2026-PR18 | 05 SOUTHWEST | 526498 | LG-MEADOW+ 2 | 69 | 2.0589 | 2.0594 | 0.0005
GEN-2026-PR18 | 05 SOUTHWEST | 526056 | E_LEVELLAND2 | 69 | 1.7522 | 1.7526 | 0.0004
GEN-2026-PR18 | 05 SOUTHWEST | 526770 | OZARK_MAHO 2 | 69 | 1.8823 | 1.8827 | 0.0004
GEN-2026-PR18 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.4519 | 2.4522 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 3.0103 | 3.0106 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525664 | LC-SPD&HART2 | 69 | 2.7794 | 2.7797 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525678 | W_ANTON 2 | 69 | 2.4755 | 2.4758 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525708 | MIDAMERI#2 2 | 69 | 2.5635 | 2.5638 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525717 | WHITHARRAL 2 | 69 | 2.4915 | 2.4918 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.8932 | 3.8935 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 526631 | LAKEVIEW 2 | 69 | 1.583 | 1.5833 | 0.0003
GEN-2026-PR18 | 05 SOUTHWEST | 525592 | SUDANRURAL 2 | 69 | 1.8973 | 1.8975 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525599 | LC-SANDHLL+2 | 69 | 2.1998 | 2.2 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525666 | LC-HARTCAMP2 | 69 | 1.7957 | 1.7959 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525701 | PHLLPPMP#2 2 | 69 | 1.8127 | 1.8129 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525703 | YELLOWHOUSE2 | 69 | 2.1868 | 2.187 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525730 | SP-ABTHY+ 2 | 69 | 2.9662 | 2.9664 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525731 | SP-ABERNTH+2 | 69 | 3.1685 | 3.1687 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525732 | SP-ABERNTHY2 | 69 | 3.1664 | 3.1666 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 3.1786 | 3.1788 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525898 | SP-SHALLWTR2 | 69 | 2.4329 | 2.4331 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525899 | SP-SHALWTR+2 | 69 | 2.565 | 2.5652 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 526630 | LG-LAKEVEW+2 | 69 | 1.1365 | 1.1367 | 0.0002
GEN-2026-PR18 | 05 SOUTHWEST | 525602 | LC-AMHERST 2 | 69 | 1.5927 | 1.5928 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525722 | OXY_ANTN_TP2 | 69 | 2.0648 | 2.0649 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.3162 | 2.3163 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525733 | SP-CNTYLINE2 | 69 | 1.9002 | 1.9003 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525734 | SP-CTN_CNTR2 | 69 | 1.8213 | 1.8214 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.6318 | 2.6319 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525744 | LH-HALECTR 2 | 69 | 1.2949 | 1.295 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525745 | LH-HALECTR+2 | 69 | 1.5587 | 1.5588 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.6735 | 2.6736 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525854 | LH-WILSON 2 | 69 | 2.0679 | 2.068 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525855 | LH-ELLEN 2 | 69 | 1.4538 | 1.4539 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525859 | SP-BECTON+ 2 | 69 | 1.7581 | 1.7582 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525860 | SP-BECTONTP2 | 69 | 2.372 | 2.3721 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525891 | WHITEHEAD 2 | 69 | 3.0724 | 3.0725 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 526073 | STANTON_N 2 | 69 | 2.1026 | 2.1027 | 0.0001
GEN-2026-PR18 | 05 SOUTHWEST | 525724 | COUNTYLINE 2 | 69 | 2.0606 | 2.0606 | 0