## Executive Summary
Executive Summary: Group 03 GEN-2026-PR7 Priority Process Study
Interconnection Customer GEN-2026-PR7 (Group 03) has requested a Priority System Impact Study pursuant to Section 3.11 of the GIP under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.1 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR7 generation for total of:
39.76 MW
The minimum cost of interconnecting GEN-2026-PR7 included in this Priority Process is estimated at:
Total Network Upgrade $0 Steady State Network Upgrade $0 Stability Network Upgrade $0 Steady State/Stability Network Upgrade $0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR7 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 8/10/2026
Costs for Wind Requests were allocated using the 29L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4624400% | SPP | Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.9 | ER | MIDW | South Hays 230kV | SPECIAL STUDY
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | SPECIAL STUDY
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | SPECIAL STUDY
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | SPECIAL STUDY
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | SPECIAL STUDY
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR7 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 39.76 | 0 | Non-Convergence ftlo P42:345:SPS:CARPENTER-OR335:::EHV: | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 39.76 | 39.76
GEN-2026-PR7 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 39.76 | 0 | Non-Convergence ftlo P42:345:SPS:CARPENTER-OR335:::EHV: | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 39.76 | 39.76
GEN-2026-PR7 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 39.76 | 0 | 532765 HOYT 7 345 532766 JEC N 7 345 1 ftlo System Intact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 39.76 | N/A
GEN-2026-PR7 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 39.76 | 0 | 532765 HOYT 7 345 532766 JEC N 7 345 1 ftlo System Intact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 39.76 | N/A
GEN-2026-PR7 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 39.76 | 0 | Non-Convergence ftlo P42:345:SPS:CARPENTER-OR335:::EHV: | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 39.76 | 39.76
GEN-2026-PR7 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 39.76 | 0 | Non-Convergence ftlo P42:345:SPS:CARPENTER-OR335:::EHV: | Multiple Upgrades | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 39.76 | 39.76
GEN-2026-PR7 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 39.76 | 0 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 ftlo System Intact | Rebuild the FINNEY 7 to G23-015-TAP 345kV Line 1 | N/A | N/A | N/A | 49.68 | N/A | N/A | N/A | N/A | N/A | 39.76
GEN-2026-PR7 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 39.76 | 0 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 ftlo System Intact | Rebuild the FINNEY 7 to G23-015-TAP 345kV Line 1 | N/A | N/A | N/A | 49.68 | N/A | N/A | N/A | N/A | N/A | 39.76

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
03ALL | GEN-2026-PR7 PSIS | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29L | System Intact | 956 | 956 | 102.02 | 102.48 |  |  |  | Rebuild the FINNEY 7 to HOLCOMB7 345kV Line 1
03ALL | GEN-2026-PR7 PSIS | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29L | System Intact | 956 | 956 | 114.02 | 114.48 |  |  |  | Rebuild the FINNEY 7 to G23-015-TAP 345kV Line 1
03ALL | GEN-2026-PR7 PSIS | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 26SP, 29SP, 29WP | System Intact | 830 | 830 | 131.74 | 131.94 |  |  |  | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
03ALL | GEN-2026-PR7 PSIS | ERIS | Non-Converged | Non-Convergence | 29L | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | Multiple Upgrades
03ALL | GEN-2026-PR7 PSIS | ERIS | Non-Converged | Non-Convergence | 29L | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | Multiple Upgrades
03ALL | GEN-2026-PR7 PSIS | ERIS | Non-Converged | Non-Convergence | 29L | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | Multiple Upgrades
03ALL | GEN-2026-PR7 PSIS | ERIS | Non-Converged | Non-Convergence | 29L | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | [7 empty] | Multiple Upgrades
03ALL | GEN-2026-PR7 PSIS | ERIS | Non-Converged | Non-Convergence | 29L | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | [7 empty] | Multiple Upgrades
03ALL | GEN-2026-PR7 PSIS | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
03ALL | GEN-2026-PR7 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
03ALL | GEN-2026-PR7 PSIS CF | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 29L | System Intact | 330 | 350 | 130.86 | 131 |  |  |  | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
03ALL | GEN-2026-PR7 PSIS CF | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 26SP, 29SP | 640065 AXTELL 3 345 640527 MACON 3 345 1 | 330 | 350 | 102.01 | 104.21 |  |  |  | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
03ALL | GEN-2026-PR7 PSIS CF | ERIS | Thermal | None | 29WP | None | [7 empty] | None
03ALL | GEN-2026-PR7 PSIS CF | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
03ALL | GEN-2026-PR7 PSIS CF | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
03ALL | GEN-2026-PR7 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
03ALL | GEN-2026-PR7 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to G23-015-TAP 345kV Line 1 | Contingent | Rebuild the existing FINNEY 7 to G23-015-TAP 345 kV line 1 (7.36 miles) to a minimum rating of 1793 MVA | 0 | 0% | 16192000 | 0.13035
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV Line 1 | Contingent | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 1 (0.75 miles) to a minimum rating of 1793 MVA | 0 | 0% | 1650000 | 0.13035
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | Rebuild the HOYT 7 to JEC N 7 345kV Line 1 | Contingent | Rebuild the existing HOYT 7 to JEC N 7 345 kV line 1 (24.3 miles) to a minimum rating of 1616 MVA | 0 | 0% | 53460000 | 0.04309
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | Hitchland-Carpenter 345 kV New Line ckt P2 | Contingent | Build a new Hitchland to Carpenter 345 kV line P2 (50.02 miles) to a standard rating of 1098 MVA | 0 | 0% | 165062000 | 0.12785
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | Carpenter-G23-015-TAP 34 5kV New Line ckt P2 | Contingent | Build a new Carpenter to G23-015-TAP 345 kV line P2 (60.6 miles) to a standard rating of 956 MVA | 0 | 0% | 197860000 | 0.12785
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | Holcomb-Sidney 345 kV New Line ckt P2 | Contingent | Build a new Holcomb to Sidney 345 kV line P2 (300 miles) to a standard rating of 1792 MVA | 0 | 0% | 940000000 | 0.12785
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | South Hays 230kV Substation GEN-2026-PR17 Interconnection (TOIF) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR7 (39.76/Wind), into South Hays 230kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR7 | GEN-2026-PR7 PSIS | 03 CENTRAL | TBD | ERIS | South Hays 230kV Substation GEN-2026-PR17 Interconnection (Non-Shared NU) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR7 (39.76/Wind), into South Hays 230kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR7 | GEN-2026-PR7 PSIS CF | 03 CENTRAL | 500789 | ERIS | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Contingent | Rebuild 22.45 miles of 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 0 | 0% | 42654300.12 | N/A
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Hitchland-Carpenter 345 kV New Line ckt P2 | TBD | Build a new Hitchland to Carpenter 345 kV line P2 (50.02 miles) to a standard rating of 1098 MVA | SPS | 36 | 165062000
Contingent | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Carpenter-G23-015-TAP 345kV New Line ckt P2 | TBD | Build a new Carpenter to G23-015-TAP 345 kV line P2 (60.6 miles) to a standard rating of 956 MVA | SPS | 36 | 197860000
Contingent | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Holcomb-Sidney 345 kV New Line ckt P2 | TBD | Build a new Holcomb to Sidney 345 kV line P2 (300 miles) to a standard rating of 1792 MVA | SUNC/WAPA | 36 | 940000000
Contingent | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild the FINNEY 7 to G23-015-TAP 345kV Line 1 | TBD | Rebuild the existing FINNEY 7 to G23-015-TAP 345 kV line 1 (7.36 miles) to a minimum rating of 1793 MVA | SPS | 36 | 16192000
Contingent | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV Line 1 | TBD | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 1 (0.75 miles) to a minimum rating of 1793 MVA | SPS/SUNC | 36 | 1650000
Contingent | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild the HOYT 7 to JEC N 7 345kV Line 1 | TBD | Rebuild the existing HOYT 7 to JEC N 7 345 kV line 1 (24.3 miles) to a minimum rating of 1616 MVA | WERE | 36 | 53460000
Interconnection | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | GEN-2026-PR7 PSIS | ERIS | South Hays 230kV Substation GEN-2026-PR17 Interconnection (TOIF) (MIDW) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR7 (39.76/Wind), into South Hays 230kV Substation | MIDW | TBD | TBD
Interconnection | GEN-2026-PR7 PSIS | Steady State | 03 CENTRAL | GEN-2026-PR7 PSIS | ERIS | South Hays 230kV Substation GEN-2026-PR17 Interconnection (Non-Shared NU) (MIDW) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR7 (39.76/Wind), into South Hays 230kV Substation | MIDW | TBD | TBD
Contingent | GEN-2026-PR7 PSIS CF | Steady State | 03 CENTRAL | ITP2025 | ERIS | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | 500789 | Rebuild 22.45 miles of 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | WERE |  | 42654300.12
1416878300.12

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504180 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem 765 kV Reactor | Install 150 MVAR reactor at Anthem 765 kV substation | 2025 ITP | Yes | N/A | 0.05646 | 4821400% | 15000000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 500754 | Carpenter 345 kV New Capacitor | Carpenter 345 kV Capacitor | Install 90 MVAR capacitor at Carpenter 345 kV substation | 2025 ITP | Yes | N/A | 0.05337 | 4727000% | 5126042.73
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504223 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV Reactor | Install 375 MVAR reactor at Crawfish Draw 765 kV substation | 2025 ITP | Yes | N/A | 0.04092 | 4780500% | 12271304.934
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 502193 | Oklaunion - Crawfish Draw 345 kV New Line Woodward - Hitchland 345 kV New Line Beckham Co - Crawfish Draw 345 kV New Line Hitchland - Potter Co 345 kV New Line Potter Co - Crawfish Draw 345 kV Double-Circuit New Line Tolk - Crawfish Draw 345 kV New Line Crawfish Draw - Yoakum 345 kV Double-Circuit New Line Crawfish Draw - Eddy Co 345 kV Double-Circuit New Line Yoakum - Hobbs 345 kV Double-Circuit New Line Gaines - Hobbs 345 kV New Line Gaines - Andrews 345 kV New Line Crossroads - Phantom 765 kV Line Tap Eddy Co - Kiowa 345 kV New Line Hobbs - Phantom 345 kV Double-Circuit New Line Hobbs - Road Runner 345 kV Double-Circuit Line Tap Kiowa - Phantom 345 kV Double-Circuit New Line Kiowa - Road Runner 345 kV Line Tap Phantom - Road Runner 345 kV New Line Phantom - Malaga Bend 345 kV New Line North Loving - Malaga Bend 345 kV New Line China Draw - Battle Axe 345 kV New Line Andrews - Ponderosa 345 kV New Line Sage Brush - Inola 345 kV New Line Battle Axe - Ponderosa 345 kV New Line Yoakum 115 kV New SVC Eddy Co 115 kV New SVC Sage Brush 115 kV New SVC North Loving 345 kV New SVC Lea National 115 kV New SVC Sage Brush 345 kV New Substation Inola 345 kV New Substation Malaga Bend 345 kV New Substation Kiowa 765 kV New Substation Battle Axe 345 kV New Substation Ponderosa 345 kV New Substation Sand Dunes 345 kV New Substation PCA 115 kV New Capacitor Medanos 115 kV New Capacitor XTO Tap 115 kV New Capacitor Quahada 115 kV New Capacitor Ward 115 kV New Capacitor Tolk 230/345 kV New Transformer Chaves Co 115/230 kV New Transformer Sage Brush 115/345 kV New Transformer Potash Junction 115/230 kV New Transformer Kiowa 345/115 kV New Transformer Kiowa 345/765 kV New Transformer Phantom 115/345 kV New Transformer Sand Dunes 115/345 kV New Transformer Battle Axe 115/345 kV New Transformer Malaga Bend 115/345 kV New Transformer China Draw 115/345 kV New Transformer Ponderosa 115/345 kV New Transformer Andrews 115/345 kV New Transformer | Hitchland 345 kV Reactor | Install 52.36 MVAR reactor at Hitchland 345 kV substation | 2025 ITP | Yes | N/A | 0.05941 | TBD | 5236000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504247 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Potter Co 765 kV Reactor | Install 225 MVAR reactor at Potter Co 765 kV substation | 2025 ITP | Yes | N/A | 0.04464 | 4821400% | 22500000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504257 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Reactor | Install 150 MVAR reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.04738 | 4780500% | 15000000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504302 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Reactor | Install 150 MVAR reactor at Viola 765 kV substation | 2025 ITP | Yes | N/A | 0.05646 | 4821400% | 266653225
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504304 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | 0.03086 | 4821400% | 104567202
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504243 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.04092 | 4821400% | 30000000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504162 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem - Seminole 765 kV Ckt 1 New Line | Build a 131.4-mile 765 kV Ckt 1 line from Anthem to Seminole | 2025 ITP | Yes | N/A | 0.04738 | 4821400% | 762120000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504296 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 180.1-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | 0.05646 | 4821600% | 1044580000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 502608 | Line - North Hays – Chetolah Creek 115 kV New Line | North Hays - Chetolah Creek 115 kV Ckt 1 New Line | Build a 8-mile 115 kV Ckt 1 line from North Hays to Chetolah Creek | 2025 ITP | Yes | N/A | 0.07635 | 4725600% | 21559257.04
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 500077 | Line - Knoll - North Hays 115 kV Rebuild | Knoll - North Hays 115 kV Ckt 1 Rebuild | Rebuild 2-mile Ckt 1 line from Knoll 115 kV substation to North Hays 115 kV substation | 2025 ITP | Yes | N/A | 0.07635 | 4689100% | 2600000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 500789 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 22.45 miles of 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | N/A | 0.14808 | 4707500% | 42654300.12
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | 504279 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward - Crawfish Draw 765 kV Ckt 1 New Line | Build a 263.6-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw | 2025 ITP | Yes | N/A | 0.04092 | 4821400% | 1528880000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | TBD | Build the Daykin 345 kV Substation | Build the Daykin 345 kV Substation | Tap the new Tobias to Elm Creek 345 kV line and build a 345 kV Substation (Daykin) | DISIS-2023-001 | Yes | N/A | 0.03456 | TBD (36-month lead time) | 23000000
GEN-2026-PR7 | 03 CENTRAL | ER | 210680 | 143660/143661/143662 | S3454 - S3740 345 kV New Line | Line - S3454 - S3740 345 kV | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | N/A | 0.04057 | TBD (18-month lead time) | 151169707
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | N/A | -0.04081 | TBD (36-month lead time) | $ 96,000,000.00
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | N/A | -0.06131 | TBD (36-month lead time) | 102596000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | TBD | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | DISIS-2018-001 | Yes | N/A | 0.03293 | TBD (36-month lead time) | 240000
GEN-2026-PR7 | 03 CENTRAL | ER | TBD | TBD | Seward to St. John 115 kV Terminal Equipment Upgrade | Seward to St. John 115 kV Terminal Equipment Upgrade | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | DISIS-2018-002/2019-001 | Yes | N/A | 0.03967 | TBD (36-month lead time) | 240000

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR7 | 03 CENTRAL | Yes | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 0.01307 | 0.51966 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | 0.00771 | 0.30655 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.02001 | -0.7956 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.02001 | -0.7956 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.0134 | -0.53278 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.05141 | 2.0441 | Yes
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.03114 | 1.2381 | Yes
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 0.00136 | 0.054074 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 0.00136 | 0.054074 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.01098 | 0.43656 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.01067 | 0.42424 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.02827 | 1.124 | Yes
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.01724 | 0.68546 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00519 | -0.20635 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00519 | -0.20635 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 0.00491 | 0.19522 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.02028 | -0.80633 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00252 | 0.1002 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00252 | 0.1002 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.02128 | 0.84609 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00561 | 0.22305 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00349 | 0.13876 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00583 | 0.2318 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 0.00117 | 0.046519 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 0.00117 | 0.046519 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 0.00117 | 0.046519 | No
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 0.00117 | 0.046519 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR7 | 03 CENTRAL | G03 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR7 PSIS | 03ALL | 1 | 26SP | GEN-2026-PR7 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 830 | 830 | 0.03806 | 119.13 | System Intact | TDF Impact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
Thermal | GEN-2026-PR7 PSIS | 03ALL | 1 | 29L | GEN-2026-PR7 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 956 | 956 | 0.12785 | 114.48 | System Intact | TDF Impact | Rebuild the FINNEY 7 to G23-015-TAP 345kV Line 1
Thermal | GEN-2026-PR7 PSIS | 03ALL | 1 | 29L | GEN-2026-PR7 | TO->FROM | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956 | 956 | 0.12785 | 102.48 | System Intact | TDF Impact | Rebuild the FINNEY 7 to HOLCOMB7 345kV Line 1
Thermal | GEN-2026-PR7 PSIS | 03ALL | 1 | 29SP | GEN-2026-PR7 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 830 | 830 | 0.04365 | 131.94 | System Intact | TDF Impact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
Thermal | GEN-2026-PR7 PSIS | 03ALL | 1 | 29WP | GEN-2026-PR7 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 830 | 830 | 0.03748 | 106.2 | System Intact | TDF Impact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.12785 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | Hitchland-Carpenter 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.12785 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Hitchland-Carpenter 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.12785 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | Holcomb-Sidney 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.12785 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Holcomb-Sidney 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.12785 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | Carpenter-G23-015-TAP 345kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.12785 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Carpenter-G23-015-TAP 345kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.04365 |  | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Hitchland-Carpenter 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.03806 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | Hitchland-Carpenter 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.03748 |  | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Hitchland-Carpenter 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.04365 |  | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Holcomb-Sidney 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.03806 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | Holcomb-Sidney 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.03748 |  | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Holcomb-Sidney 345 kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.04365 |  | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Carpenter-G23-015-TAP 345kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.03806 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | Carpenter-G23-015-TAP 345kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29L | GEN-2026-PR7 | " | Non-Converged |  |  | 0.03748 |  | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Carpenter-G23-015-TAP 345kV New Line ckt P2
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR7 PSIS | 03ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR7 Expanded Scope | 03ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR7 Expanded Scope | 03ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR7 Expanded Scope | 03ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR7 Expanded Scope | 03ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 26SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20147 | 101.43 | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 26SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20141 | 100.87 | 640065 AXTELL 3 345 640527 MACON 3 345 1 | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 26SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20141 | 100.43 | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 26SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20141 | 100.43 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 26SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20141 | 100.4 | 640527 MACON 3 345 777450 G24-016-TAP 345 1 | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29L | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.14718 | 131 | System Intact | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20136 | 104.21 | 640065 AXTELL 3 345 640527 MACON 3 345 1 | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20137 | 104.12 | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20136 | 103.77 | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20136 | 103.77 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29SP | GEN-2026-PR7 | FROM->TO | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 330 | 350 | 0.20136 | 103.75 | 640527 MACON 3 345 777450 G24-016-TAP 345 1 | TDF Impact | Smokey Hills - Summit 230 kV Ckt 1 Rebuild
Non-Converged | GEN-2026-PR7 PSIS CF | 03ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR7 PSIS CF | 03ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR7 PSIS CF | 03ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR7 PSIS CF | 03ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR7 PSIS CF | 03ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR7 PSIS | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS | 03ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS | 03ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS | 03ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS CF | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS CF | 03ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS CF | 03ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR7 PSIS CF | 03ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on VINEDE_S 115.00 (530722) 115 kV Bus a. Apply fault at the VINEDE_S 115.00 (530722) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.2. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.3. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.4. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on GMEC 3 115.00 (530676) 115 kV Bus a. Apply fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708), G16-160-GEN1 (588451). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips SMKYP2G1 (530600). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on SMKYP1 6 230.00 (530593) 230 kV Bus a. Apply fault at the SMKYP1 6 230.00 (530593) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.2. SMKYP1 6 (530593) 230.0 kV to SHP134 1 (530633) 34.5 kV to MPT TERT (530726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634). Frequency protection trips SMKYP2G1 (530600), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips SMKYP2G1 (530600). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BUNKRHL3 115.00 (539643) 115 kV Bus a. Apply fault at the BUNKRHL3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.4. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips CEDAR_BLU_G1 (930986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-075GEN1 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601), SSWIND 1 (539100). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). Frequency protection trips SVWF3 1 (539120). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MACON 3 (640527) 345.0 kV to LITTLEBLUEW3 (640528) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on G19-053/055 230.00 (763846) 230 kV Bus a. Apply fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G22-065GEN1 (768284), G19-053-GEN1 (763849), G19-055-GEN2 (763872). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on G19-054/068 230.00 (763857) 230 kV Bus a. Apply fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), G19-054-GEN2 (763861). Frequency protection trips G19-068-GEN1 (763970), G19-054-GEN1 (763860). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-075-TAP (768480) 345.0 kV to GEN-2022-075 (768481) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_082 | 3 Phase fault on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_083 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_084 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_085 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_086 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_087 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_088 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_089 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_090 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_091 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_092 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_093 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844), G17-221-GEN1 (760307). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_094 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844), G17-221-GEN1 (760307). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_095 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_096 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_097 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_098 | 3 Phase fault on NRSS7 345.00 (532777) 345 kV Bus a. Apply fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_099 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_100 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844), G17-221-GEN1 (760307). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_101 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_102 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_103 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_104 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_105 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_106 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_107 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601), BUFF_DN_G11 (523062), BUFF_DN_G21 (523061). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_108 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_109 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G21-006-GEN1 (765352), G21-006-GEN2 (765355). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_110 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_111 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_112 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_113 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_114 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_115 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). Frequency protection trips G11-008-GEN7 (539858), G19-058-GEN2 (763895), G19-063-GEN1 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_116 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). Frequency protection trips G11-008-GEN7 (539858), G19-058-GEN2 (763895), G19-063-GEN1 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_117 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to PIXLEY-SOLAR (539871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips PIXLEY-SOL1 (539874), PIXLEY-SOL2 (539877). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_118 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2018-049 (762834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_119 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_120 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_121 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_122 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3771 (640600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_123 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_124 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_125 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_126 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_127 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_128 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_129 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_130 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_131 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_132 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_133 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips PIXLEY-SOL1 (539874), PIXLEY-SOL2 (539877). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_134 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_135 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215), 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_136 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips PIXLEY-SOL1 (539874), PIXLEY-SOL2 (539877). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNLL1 1 (530629) 11.5 kV to KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply Fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.5. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 b.6. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.5. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.8. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.6. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.7. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.6. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.7. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CEDARBLF_COL34.500 (530613) 34.5 kV Bus a. Apply Fault at the CEDARBLF_COL34.500 (530613) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.5. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.6. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LITTLEBLUWG1 (643311), LITTLEBLUWS1 (643310). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on PRWNDCL1 34.500 (530701) 34.5 kV Bus a. Apply Fault at the PRWNDCL1 34.500 (530701) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.6. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 b.8. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.10. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips PRWINDG1 (530690). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.6. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.7. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.8. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.9. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.10. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.11. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.12. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.13. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.4. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.5. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.7. CDRBLF_13.8 (530611) 13.8 kV to CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV Three Winding #1 b.9. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.11. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.12. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.13. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.14. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.16. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.17. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614), CEDAR_BLU_G1 (930986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MACON 3345.00 (640527) 345 kV Bus a. Apply Fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LITTLEBLUWG1 (643311), LITTLEBLUWS1 (643310). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips RUSL_SOL (539601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SVWF3 1 (539120), SVWF2 1 (539136). Frequency protection trips SVWF1 1 (539116). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SVWF3 1 (539120), SVWF2 1 (539136). Frequency protection trips SVWF1 1 (539116). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.2. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDT1 (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.8. SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.9. SPERVLT1 (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.10. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.12. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLD1 (539936) 13.8 kV Three Winding #1 b.13. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.14. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1 1 (539116) 0.6 kV Two Winding #1 b.15. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SVWF3 1 (539120), SVWF2 1 (539136). Frequency protection trips SVWF1 1 (539116). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on ELLSWTH3 115.00 (539662) 115 kV Bus a. Apply Fault at the ELLSWTH3 115.00 (539662) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. ELLSWTH3 (539662) 115.0 kV to ELLSWTH1 (539708) 34.5 kV to ELSWTH-1 (539908) 13.8 kV Three Winding #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.6. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply Fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.6. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 b.5. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.6. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-1 (539938) 7.2 kV Three Winding #1 b.7. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips RUSL_SOL (539601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on ST-JOHN3 115.00 (539696) 115 kV Bus a. Apply Fault at the ST-JOHN3 115.00 (539696) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.2. SADLHRN3 (539010) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. ST-JOHN3 (539696) 115.0 kV to GEN-2024-205 (783121) 115.0 kV Transmission Circuit #1 b.5. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.6. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.7. SADLHRN3 (539010) 115.0 kV to PRICHRD3 (539648) 115.0 kV Transmission Circuit #1 b.8. PRICHRD3 (539648) 115.0 kV to RVROAD 3 (539651) 115.0 kV Transmission Circuit #1 b.9. PRICHRD3 (539648) 115.0 kV to PRATTENERGY3 (539753) 115.0 kV Transmission Circuit #1 b.10. PRICHRD3 (539648) 115.0 kV to ASGI2015-001 (584710) 115.0 kV Transmission Circuit #1 b.11. PRATTENERGY3 (539753) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.12. SEMCRDE3 (539754) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.13. SEMCRDE3 (539754) 115.0 kV to SEMCRDE1 (539755) 34.5 kV to SEMCRDE-1 (539965) 13.8 kV Three Winding #1 b.14. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.15. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.16. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.17. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-205GEN1 (783124), G24-205GEN2 (783127). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 b.4. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 b.5. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 b.7. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.8. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.9. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.10. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.3. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips DV1 WF 1 (534024), DV2 WF 1 (534025). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.4. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970). Frequency protection trips G19-054-GEN1 (763860). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.5. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.5. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.4. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.3. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBND-1 (539921) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.3. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970). Frequency protection trips G19-054-GEN1 (763860). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to FRMR CTY WF (635027) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.3. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.4. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.5. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.6. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3458 3 (645458) 345.0 kV to S3458-HOLT 3 (645558) 345.0 kV Transmission Circuit #z1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #2 b.6. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.8. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.5. G18-125-TAP (763410) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_198 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUFF_DN_G11 (523062), BUFF_DN_G21 (523061). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_199 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_200 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_201 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_202 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_203 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_205 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_206 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_207 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_208 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_209 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_211 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_212 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_213 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.8. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221-GEN1 (760307), G17-220-GEN1 (760287), K1 WF1 (534021), K2 WF1 (534022), N1 WF1 (534020), P1 WF 1 (534023). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_214 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986), G21-006-GEN1 (765352), G21-006-GEN2 (765355). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_216 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_217 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.5. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.6. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.7. WICHITA7 (532796) 345.0 kV to WICHTA11_4 (532994) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 b.8. WICHITA7 (532796) 345.0 kV to WICHTA12_4 (532997) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_218 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.3. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.4. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.5. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.6. WOLFCRK7 (532797) 345.0 kV to WCGS_TX1_1 (533900) 13.8 kV to WCGS_TX1TER1 (533901) 4.0 kV Three Winding #1 b.7. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 b.8. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX9_T1 (533905) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WCGS U1 (532751). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_219 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FR2E1WF1 (533123), FR2E2WF1 (533124), FR2W1WF1 (533125), FR2W2WF1 (533126). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_220 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_221 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_222 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_223 | Single Phase Fault with Stuck Breaker on NRSS7 345.00 (532777) 345 kV Bus a. Apply Fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHORDGWF7 (532778) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips NR1 WF1 (532712), NR2 WF1 (532713), NR3 WF1 (532715), NR4 WF1 (532714). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_224 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_225 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_226 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_227 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_228 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_229 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_230 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_231 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.3. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_232 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_233 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.3. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_234 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_235 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_236 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.2. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 b.3. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_237 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Line to Ground Fault on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to Trip Bus #1 b.7. HILLCTY1 (531387) 34.5 kV to Generator #1 b.8. HILLCTY1 (531387) 34.5 kV to Generator #2 b.9. HILLCTY1 (531387) 34.5 kV to Generator #3 b.10. HILLCTY1 (531387) 34.5 kV to Generator #4 b.11. HILLCTY1 (531387) 34.5 kV to Generator #5 b.12. HILLCTY1 (531387) 34.5 kV to Generator #6 b.13. HILLCTY1 (531387) 34.5 kV to Trip Bus # b.14. REDLIN 3 (530605) 115.0 kV to Trip Bus # b.15. HOXIE 3 (530556) 115.0 kV to Trip Bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Line to Ground Fault on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Breaker at From Bus #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Breaker at From Bus #1 b.3. N HAYS3 (530581) 115.0 kV to Trip Bus #1 b.4. VINETAP3 (530693) 115.0 kV to Trip Bus #1 b.5. GMECG1 1 (530674) 13.8 kV to Trip Bus #1 b.6. GMECG2 1 (530675) 13.8 kV to Trip Bus #1 b.7. GMEC 3 (530676) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. ANGUS 3 (530714) 115.0 kV to Trip Bus # b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. GORHAM 3 (530552) 115.0 kV to Load #1 b.8. RUSLPMP3 (530684) 115.0 kV to Load #1 b.9. GORHAM 3 (530552) 115.0 kV to Trip Bus # b.10. RUSLPMP3 (530684) 115.0 kV to Trip Bus # b.11. PFEIFER 3 (530725) 115.0 kV to Load #1 b.12. PFEIFER 3 (530725) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to Trip Bus # b.4. BUCKW_WTG (530708) 0.7 kV to Trip Bus # b.5. BUCKEYE_230 (530702) 230.0 kV to Trip Bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to Trip Bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to Trip Bus # b.8. BUCKW_TERT (530706) 13.8 kV to Trip Bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to Trip Bus # b.10. BUCKE_TERT (530709) 13.8 kV to Trip Bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to None Transmission Circuit #1 b.3. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.4. None to Trip Bus # b.5. SHP234 1 (530604) 34.5 kV to Trip Bus # b.6. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.7. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634). Frequency protection trips SMKYP2G1 (530600), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.4. SMKYP1 6 (530593) 230.0 kV to Trip Bus # b.5. SHP134 1X (530595) 34.5 kV to Trip Bus # b.6. SHP134 1 (530633) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634). Frequency protection trips SMKYP2G1 (530600), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to Trip Bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.7. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.8. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.9. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.10. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970), BCVI WTG (520522), CHSVWEG1 (515926), CHSVWWG1 (515927), SLATEGEN1 (533141), GI96_GEN (99964), RKYRDGW2-0 (511970). Frequency protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on VINEDE_S 115.00 (530722) 115 kV Bus a. Apply fault at the VINEDE_S 115.00 (530722) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.2. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.3. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.4. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on GMEC 3 115.00 (530676) 115 kV Bus a. Apply fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ATTALA G1 (337006), 1ATTALA G2 (337007), 1ATTALA S1 (337008), J2027 GEN (50270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708), G16-160-GEN1 (588451). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips SMKYP2G1 (530600). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on SMKYP1 6 230.00 (530593) 230 kV Bus a. Apply fault at the SMKYP1 6 230.00 (530593) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.2. SMKYP1 6 (530593) 230.0 kV to SHP134 1 (530633) 34.5 kV to MPT TERT (530726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips SMKYP2G1 (530600), SMKYP1V80 (530594), SMKYP1V100 (530634). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G11-008-GEN7 (539858), G19-054-GEN2 (763861), G19-068-GEN1 (763970), BCVI WTG (520522), CHSVWEG1 (515926), G19-058-GEN2 (763895), CHSVWWG1 (515927), G19-053-GEN1 (763849), G19-063-GEN1 (763926), MRWY-WG2 (539105), G19-055-GEN2 (763872). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips SMKYP2G1 (530600). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LITTLEBLUWG1 (643311), LITTLEBLUWS1 (643310). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), BCVI WTG (520522), CHSVWEG1 (515926), CHSVWWG1 (515927), MRWY-WG1 (539103), MRWY-WG2 (539105), G22-075GEN1 (768484), G18-057-GEN1 (762925), GI96_GEN (99964), FLTRDG1-WG11 (539114). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883), RTLSNAK.GN1W (643269), RTLSNAK.GN2W (643270), G287 NOB1G W (600101), G287 NOB2G W (600112), G287 NOB3G W (600113), G287 NOB4G W (600114), BROOKE WF (631215). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970), BCVI WTG (520522), CHSVWEG1 (515926), CHSVWWG1 (515927), SLATEGEN1 (533141), GI96_GEN (99964), RKYRDGW2-0 (511970). Frequency protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BUNKRHL3 115.00 (539643) 115 kV Bus a. Apply fault at the BUNKRHL3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.4. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips CEDAR_BLU_G1 (930986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-075GEN1 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), G11-008-GEN7 (539858), CNTRPL-WTG1 (531601), MRWY-WG1 (539103), G22-075GEN1 (768484), RTLSNAK.GN1W (643269). Frequency protection trips RTLSNAK.GN2W (643270). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G11-008-GEN7 (539858), G19-054-GEN2 (763861), G19-068-GEN1 (763970), CNTRPL-WTG1 (531601), BCVI WTG (520522), G19-058-GEN2 (763895), G19-063-GEN1 (763926), G18-057-GEN1 (762925), G23-033GEN1 (772644), G23-033GEN2 (772647), G23-037GEN1 (772724), G23-037GEN2 (772727). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G11-008-GEN7 (539858), G19-054-GEN2 (763861), G19-068-GEN1 (763970), CNTRPL-WTG1 (531601), CHSVWEG1 (515926), G19-058-GEN2 (763895), CHSVWWG1 (515927), G19-053-GEN1 (763849), G19-063-GEN1 (763926), MRWY-WG1 (539103), MRWY-WG2 (539105), G19-055-GEN2 (763872), SLATEGEN1 (533141). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), G11-008-GEN7 (539858), CNTRPL-WTG1 (531601), G19-058-GEN2 (763895), G19-053-GEN1 (763849), G19-063-GEN1 (763926), G19-055-GEN2 (763872), G22-075GEN1 (768484), FLTRDG1-WG11 (539114). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), SVWF3 1 (539120). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MACON 3 (640527) 345.0 kV to LITTLEBLUEW3 (640528) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LITTLEBLUWG1 (643311), LITTLEBLUWS1 (643310). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on G19-053/055 230.00 (763846) 230 kV Bus a. Apply fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-053-GEN1 (763849), G19-055-GEN2 (763872), G19-055-GEN1 (763871). Frequency protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G22-065GEN1 (768284), G19-053-GEN1 (763849). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on G19-054/068 230.00 (763857) 230 kV Bus a. Apply fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), G19-054-GEN2 (763861), G19-068-GEN1 (763970). Frequency protection trips G19-054-GEN1 (763860). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-075-TAP (768480) 345.0 kV to GEN-2022-075 (768481) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_082 | 3 Phase fault on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_083 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_084 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_085 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_086 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_087 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_088 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_089 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_090 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_091 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_092 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_093 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), G11-008-GEN7 (539858), G19-054-GEN2 (763861), G19-068-GEN1 (763970), BCVI WTG (520522), CHSVWEG1 (515926), G19-058-GEN2 (763895), CHSVWWG1 (515927), G19-053-GEN1 (763849), G19-063-GEN1 (763926), MRWY-WG1 (539103), MRWY-WG2 (539105), G19-055-GEN2 (763872), G22-075GEN1 (768484), SLATEGEN1 (533141), GI96_GEN (99964), G17-221-GEN1 (760307), G21-006-GEN1 (765352), G21-006-GEN2 (765355), NR1 WF1 (532712), NR2 WF1 (532713), NR3 WF1 (532715), NR4 WF1 (532714), RKYRDGW2-0 (511970), K1 WF1 (534021), K2 WF1 (534022), N1 WF1 (534020), P1 WF 1 (534023), AB2-070 GEN1 (276668), AE2-035 GEN (276612), ARMFTG11 (515697), AURORA WIND (660055), BRULE WIND (660065), E1 WF1 (534051), E2 WF1 (534055), ER1 WF1 (534026), G18-031GEN1 (762672), G18-128-GEN1 (763420), G20-007-GEN5 (766274), G20-007-GEN6 (766277), G20-007-GEN7 (766280), G20-007-GEN8 (766283), G502 OLIVER1 (608819), IC_WF1_1 (534072), J1 WF1 (534099), J1444 GEN (44440), J1445 GEN (44450), J1572 GEN1 (45721), J183 PROSEW1 (600149), J183 PROSEW2 (600150), J2091 GEN1 (50910), J2091 GEN2 (50911), J2276 GEN (52760), J476 (637081), MARSHGEN1 (532904), MMTHPWG1 (515903), OSBORN_G1_1 (541503), R1 WF 1 (534042), R2 WF1 (534045), RKYRDGW1-0 (511971), SC_WF1_1 (534064), SC_WF2_1 (534065), SHOLES.GEN.W (643253). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_094 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284), G11-008-GEN7 (539858), G19-054-GEN2 (763861), G19-068-GEN1 (763970), BCVI WTG (520522), CHSVWEG1 (515926), G19-058-GEN2 (763895), CHSVWWG1 (515927), G19-053-GEN1 (763849), G19-063-GEN1 (763926), MRWY-WG1 (539103), MRWY-WG2 (539105), G19-055-GEN2 (763872), G22-075GEN1 (768484), SLATEGEN1 (533141), GI96_GEN (99964), G17-221-GEN1 (760307), G21-006-GEN1 (765352), G21-006-GEN2 (765355), NR1 WF1 (532712), NR2 WF1 (532713), NR3 WF1 (532715), NR4 WF1 (532714), RKYRDGW2-0 (511970), K1 WF1 (534021), K2 WF1 (534022), N1 WF1 (534020), P1 WF 1 (534023), AB2-070 GEN1 (276668), AE2-035 GEN (276612), ARMFTG11 (515697), AURORA WIND (660055), BRULE WIND (660065), E1 WF1 (534051), E2 WF1 (534055), ER1 WF1 (534026), G18-031GEN1 (762672), G18-128-GEN1 (763420), G20-007-GEN5 (766274), G20-007-GEN6 (766277), G20-007-GEN7 (766280), G20-007-GEN8 (766283), G502 OLIVER1 (608819), IC_WF1_1 (534072), J1 WF1 (534099), J1444 GEN (44440), J1445 GEN (44450), J1572 GEN1 (45721), J183 PROSEW1 (600149), J183 PROSEW2 (600150), J2091 GEN1 (50910), J2091 GEN2 (50911), J2276 GEN (52760), J476 (637081), MARSHGEN1 (532904), MMTHPWG1 (515903), OSBORN_G1_1 (541503), R1 WF 1 (534042), R2 WF1 (534045), RKYRDGW1-0 (511971), SC_WF1_1 (534064), SC_WF2_1 (534065), SHOLES.GEN.W (643253). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_095 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_096 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_097 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_098 | 3 Phase fault on NRSS7 345.00 (532777) 345 kV Bus a. Apply fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-057-GEN1 (762925), NR1 WF1 (532712), NR2 WF1 (532713), NR3 WF1 (532715), NR4 WF1 (532714). Frequency protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_099 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_100 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BCVI WTG (520522), CHSVWEG1 (515926), MRWY-WG1 (539103), MRWY-WG2 (539105), SLATEGEN1 (533141), G18-057-GEN1 (762925), FLTRDG1-WG11 (539114), G17-221-GEN1 (760307), G17-227GEN1 (760664). Frequency protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_101 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_102 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_103 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_104 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_105 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_106 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_107 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601), BUFF_DN_G11 (523062), BUFF_DN_G21 (523061). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_108 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG1 (531601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_109 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G21-006-GEN1 (765352), G21-006-GEN2 (765355). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_110 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_111 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BCVI WTG (520522), G18-057-GEN1 (762925). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_112 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844), FR2E1WF1 (533123), FR2E2WF1 (533124), FR2W1WF1 (533125), FR2W2WF1 (533126). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_113 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986), G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_114 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_115 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). Frequency protection trips G11-008-GEN7 (539858), G19-058-GEN2 (763895). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_116 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). Frequency protection trips G11-008-GEN7 (539858), G19-058-GEN2 (763895). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_117 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to PIXLEY-SOLAR (539871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PIXLEY-SOL1 (539874), PIXLEY-SOL2 (539877). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_118 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2018-049 (762834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-049-GEN1 (762837), G18-108-GEN1 (763287). Frequency protection trips PIXLEY-SOL1 (539874), PIXLEY-SOL2 (539877). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_119 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_120 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_121 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_122 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3771 (640600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358), R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_123 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_124 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_125 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_126 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_127 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_128 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_129 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_130 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121GEN1 (761841), G17-121GEN2 (761844). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_131 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_132 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970), CHSVWEG1 (515926), CHSVWWG1 (515927). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_133 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G11-008-GEN7 (539858), BCVI WTG (520522), G19-058-GEN2 (763895), G19-063-GEN1 (763926), MRWY-WG1 (539103), MRWY-WG2 (539105), FLTRDG1-WG11 (539114). Frequency protection trips RDDRTG11 (515882), RDDRTG21 (515883). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_134 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_135 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_136 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips PIXLEY-SOL1 (539874), PIXLEY-SOL2 (539877). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNLL1 1 (530629) 11.5 kV to KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply Fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.5. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 b.6. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.5. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.8. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.6. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.7. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.6. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.7. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CEDARBLF_COL34.500 (530613) 34.5 kV Bus a. Apply Fault at the CEDARBLF_COL34.500 (530613) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.5. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.6. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LITTLEBLUWG1 (643311), LITTLEBLUWS1 (643310). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on PRWNDCL1 34.500 (530701) 34.5 kV Bus a. Apply Fault at the PRWNDCL1 34.500 (530701) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.6. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 b.8. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.10. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips PRWINDG1 (530690). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.6. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.7. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.8. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.9. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.10. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.11. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.12. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.13. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.4. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.5. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.7. CDRBLF_13.8 (530611) 13.8 kV to CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV Three Winding #1 b.9. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.11. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.12. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.13. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.14. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.16. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.17. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MACON 3345.00 (640527) 345 kV Bus a. Apply Fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LITTLEBLUWG1 (643311), LITTLEBLUWS1 (643310). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips RUSL_SOL (539601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SVWF3 1 (539120), SVWF1 1 (539116), SVWF2 1 (539136). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SVWF3 1 (539120), SVWF1 1 (539116). Frequency protection trips SVWF2 1 (539136). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.2. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDT1 (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.8. SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.9. SPERVLT1 (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.10. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.12. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLD1 (539936) 13.8 kV Three Winding #1 b.13. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.14. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1 1 (539116) 0.6 kV Two Winding #1 b.15. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SVWF3 1 (539120), SVWF1 1 (539116), SVWF2 1 (539136). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on ELLSWTH3 115.00 (539662) 115 kV Bus a. Apply Fault at the ELLSWTH3 115.00 (539662) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. ELLSWTH3 (539662) 115.0 kV to ELLSWTH1 (539708) 34.5 kV to ELSWTH-1 (539908) 13.8 kV Three Winding #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.6. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply Fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.6. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 b.5. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.6. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-1 (539938) 7.2 kV Three Winding #1 b.7. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips RUSL_SOL (539601). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on ST-JOHN3 115.00 (539696) 115 kV Bus a. Apply Fault at the ST-JOHN3 115.00 (539696) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.2. SADLHRN3 (539010) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. ST-JOHN3 (539696) 115.0 kV to GEN-2024-205 (783121) 115.0 kV Transmission Circuit #1 b.5. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.6. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.7. SADLHRN3 (539010) 115.0 kV to PRICHRD3 (539648) 115.0 kV Transmission Circuit #1 b.8. PRICHRD3 (539648) 115.0 kV to RVROAD 3 (539651) 115.0 kV Transmission Circuit #1 b.9. PRICHRD3 (539648) 115.0 kV to PRATTENERGY3 (539753) 115.0 kV Transmission Circuit #1 b.10. PRICHRD3 (539648) 115.0 kV to ASGI2015-001 (584710) 115.0 kV Transmission Circuit #1 b.11. PRATTENERGY3 (539753) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.12. SEMCRDE3 (539754) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.13. SEMCRDE3 (539754) 115.0 kV to SEMCRDE1 (539755) 34.5 kV to SEMCRDE-1 (539965) 13.8 kV Three Winding #1 b.14. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.15. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.16. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.17. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G24-205GEN1 (783124), G24-205GEN2 (783127). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 b.4. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 b.5. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 b.7. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.8. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.9. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.10. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.3. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips DV1 WF 1 (534024), DV2 WF 1 (534025). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.4. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970). Frequency protection trips G19-054-GEN1 (763860). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.5. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.5. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.4. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.3. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065GEN1 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBND-1 (539921) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.3. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G19-054-GEN2 (763861), G19-068-GEN1 (763970). Frequency protection trips G19-054-GEN1 (763860). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to FRMR CTY WF (635027) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips R26FRMRCTYW1 (635020). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.3. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.4. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.5. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.6. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3458 3 (645458) 345.0 kV to S3458-HOLT 3 (645558) 345.0 kV Transmission Circuit #z1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #2 b.6. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.8. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.5. G18-125-TAP (763410) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_198 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUFF_DN_G11 (523062), BUFF_DN_G21 (523061). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_199 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_200 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_201 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_202 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_203 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_205 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_206 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_207 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_208 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_209 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_211 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_212 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_213 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.8. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221-GEN1 (760307), K1 WF1 (534021), K2 WF1 (534022), N1 WF1 (534020), P1 WF 1 (534023), G17-220-GEN1 (760287). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_214 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986), G21-006-GEN1 (765352), G21-006-GEN2 (765355). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_216 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_217 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.5. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.6. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.7. WICHITA7 (532796) 345.0 kV to WICHTA11_4 (532994) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 b.8. WICHITA7 (532796) 345.0 kV to WICHTA12_4 (532997) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_218 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.3. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.4. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.5. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.6. WOLFCRK7 (532797) 345.0 kV to WCGS_TX1_1 (533900) 13.8 kV to WCGS_TX1TER1 (533901) 4.0 kV Three Winding #1 b.7. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 b.8. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX9_T1 (533905) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_219 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FR2E1WF1 (533123), FR2E2WF1 (533124), FR2W1WF1 (533125), FR2W2WF1 (533126). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_220 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_221 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_222 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips WAVERGEN1 (532957). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_223 | Single Phase Fault with Stuck Breaker on NRSS7 345.00 (532777) 345 kV Bus a. Apply Fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHORDGWF7 (532778) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips NR1 WF1 (532712), NR2 WF1 (532713), NR3 WF1 (532715), NR4 WF1 (532714). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_224 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_225 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_226 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_227 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_228 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986), G22-100GEN1 (768984). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_229 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986), G22-100GEN1 (768984). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_230 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1WINSLOWG1 (301358). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_231 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.3. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_232 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_233 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.3. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_234 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986), G22-100GEN1 (768984). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_235 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_236 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.2. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 b.3. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-100GEN2 (768986). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_237 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Line to Ground Fault on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to Trip Bus #1 b.7. HILLCTY1 (531387) 34.5 kV to Generator #1 b.8. HILLCTY1 (531387) 34.5 kV to Generator #2 b.9. HILLCTY1 (531387) 34.5 kV to Generator #3 b.10. HILLCTY1 (531387) 34.5 kV to Generator #4 b.11. HILLCTY1 (531387) 34.5 kV to Generator #5 b.12. HILLCTY1 (531387) 34.5 kV to Generator #6 b.13. HILLCTY1 (531387) 34.5 kV to Trip Bus # b.14. REDLIN 3 (530605) 115.0 kV to Trip Bus # b.15. HOXIE 3 (530556) 115.0 kV to Trip Bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Line to Ground Fault on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Breaker at From Bus #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Breaker at From Bus #1 b.3. N HAYS3 (530581) 115.0 kV to Trip Bus #1 b.4. VINETAP3 (530693) 115.0 kV to Trip Bus #1 b.5. GMECG1 1 (530674) 13.8 kV to Trip Bus #1 b.6. GMECG2 1 (530675) 13.8 kV to Trip Bus #1 b.7. GMEC 3 (530676) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. ANGUS 3 (530714) 115.0 kV to Trip Bus # b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. GORHAM 3 (530552) 115.0 kV to Load #1 b.8. RUSLPMP3 (530684) 115.0 kV to Load #1 b.9. GORHAM 3 (530552) 115.0 kV to Trip Bus # b.10. RUSLPMP3 (530684) 115.0 kV to Trip Bus # b.11. PFEIFER 3 (530725) 115.0 kV to Load #1 b.12. PFEIFER 3 (530725) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to Trip Bus # b.4. BUCKW_WTG (530708) 0.7 kV to Trip Bus # b.5. BUCKEYE_230 (530702) 230.0 kV to Trip Bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to Trip Bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to Trip Bus # b.8. BUCKW_TERT (530706) 13.8 kV to Trip Bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to Trip Bus # b.10. BUCKE_TERT (530709) 13.8 kV to Trip Bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips BUCKE_WTG (530705), BUCKW_WTG (530708). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to None Transmission Circuit #1 b.3. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.4. None to Trip Bus # b.5. SHP234 1 (530604) 34.5 kV to Trip Bus # b.6. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.7. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634). Frequency protection trips SMKYP2G1 (530600), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.4. SMKYP1 6 (530593) 230.0 kV to Trip Bus # b.5. SHP134 1X (530595) 34.5 kV to Trip Bus # b.6. SHP134 1 (530633) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SMKYP1V100 (530634). Frequency protection trips SMKYP2G1 (530600), SMKYP1V80 (530594). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CEDARBLF_GEN (530614). | Protection disabled with no impact to stability.
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to Trip Bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.7. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.8. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.9. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.10. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Base | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Base | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Base | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Base | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29S | Base | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Base | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Base | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Base | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Base | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS | 29W | Base | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on VINEDE_S 115.00 (530722) 115 kV Bus a. Apply fault at the VINEDE_S 115.00 (530722) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.2. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.3. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.4. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on GMEC 3 115.00 (530676) 115 kV Bus a. Apply fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on SMKYP1 6 230.00 (530593) 230 kV Bus a. Apply fault at the SMKYP1 6 230.00 (530593) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.2. SMKYP1 6 (530593) 230.0 kV to SHP134 1 (530633) 34.5 kV to MPT TERT (530726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BUNKRHL3 115.00 (539643) 115 kV Bus a. Apply fault at the BUNKRHL3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.4. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MACON 3 (640527) 345.0 kV to LITTLEBLUEW3 (640528) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on G19-053/055 230.00 (763846) 230 kV Bus a. Apply fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on G19-054/068 230.00 (763857) 230 kV Bus a. Apply fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-075-TAP (768480) 345.0 kV to GEN-2022-075 (768481) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_082 | 3 Phase fault on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_083 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_084 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_085 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_086 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_087 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_088 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_089 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_090 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_091 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_092 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_093 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_094 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_095 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_096 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_097 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_098 | 3 Phase fault on NRSS7 345.00 (532777) 345 kV Bus a. Apply fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_099 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_100 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_101 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_102 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_103 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_104 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_105 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_106 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_107 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_108 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_109 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_110 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_111 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_112 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_113 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_114 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_115 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_116 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_117 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to PIXLEY-SOLAR (539871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_118 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2018-049 (762834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_119 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_120 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_121 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_122 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3771 (640600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_123 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_124 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_125 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_126 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_127 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_128 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_129 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_130 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_131 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_132 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_133 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_134 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_135 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P1_REGIONAL_FAULT_136 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNLL1 1 (530629) 11.5 kV to KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply Fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.5. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 b.6. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.5. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.8. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.6. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.7. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.6. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.7. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CEDARBLF_COL34.500 (530613) 34.5 kV Bus a. Apply Fault at the CEDARBLF_COL34.500 (530613) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.5. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.6. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on PRWNDCL1 34.500 (530701) 34.5 kV Bus a. Apply Fault at the PRWNDCL1 34.500 (530701) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.6. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 b.8. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.10. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.6. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.7. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.8. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.9. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.10. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.11. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.12. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.13. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.4. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.5. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.7. CDRBLF_13.8 (530611) 13.8 kV to CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV Three Winding #1 b.9. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.11. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.12. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.13. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.14. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.16. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.17. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MACON 3345.00 (640527) 345 kV Bus a. Apply Fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.2. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDT1 (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.8. SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.9. SPERVLT1 (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.10. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.12. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLD1 (539936) 13.8 kV Three Winding #1 b.13. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.14. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1 1 (539116) 0.6 kV Two Winding #1 b.15. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on ELLSWTH3 115.00 (539662) 115 kV Bus a. Apply Fault at the ELLSWTH3 115.00 (539662) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. ELLSWTH3 (539662) 115.0 kV to ELLSWTH1 (539708) 34.5 kV to ELSWTH-1 (539908) 13.8 kV Three Winding #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.6. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply Fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.6. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 b.5. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.6. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-1 (539938) 7.2 kV Three Winding #1 b.7. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on ST-JOHN3 115.00 (539696) 115 kV Bus a. Apply Fault at the ST-JOHN3 115.00 (539696) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.2. SADLHRN3 (539010) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. ST-JOHN3 (539696) 115.0 kV to GEN-2024-205 (783121) 115.0 kV Transmission Circuit #1 b.5. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.6. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.7. SADLHRN3 (539010) 115.0 kV to PRICHRD3 (539648) 115.0 kV Transmission Circuit #1 b.8. PRICHRD3 (539648) 115.0 kV to RVROAD 3 (539651) 115.0 kV Transmission Circuit #1 b.9. PRICHRD3 (539648) 115.0 kV to PRATTENERGY3 (539753) 115.0 kV Transmission Circuit #1 b.10. PRICHRD3 (539648) 115.0 kV to ASGI2015-001 (584710) 115.0 kV Transmission Circuit #1 b.11. PRATTENERGY3 (539753) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.12. SEMCRDE3 (539754) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.13. SEMCRDE3 (539754) 115.0 kV to SEMCRDE1 (539755) 34.5 kV to SEMCRDE-1 (539965) 13.8 kV Three Winding #1 b.14. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.15. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.16. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.17. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 b.4. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 b.5. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 b.7. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.8. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.9. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.10. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.3. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.4. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.5. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.5. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.4. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.3. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBND-1 (539921) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.3. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to FRMR CTY WF (635027) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.3. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.4. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.5. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.6. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3458 3 (645458) 345.0 kV to S3458-HOLT 3 (645558) 345.0 kV Transmission Circuit #z1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #2 b.6. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.8. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.5. G18-125-TAP (763410) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_198 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_199 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_200 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_201 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_202 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_203 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_205 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_206 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_207 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_208 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_209 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_211 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_212 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_213 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.8. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_214 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_216 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_217 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.5. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.6. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.7. WICHITA7 (532796) 345.0 kV to WICHTA11_4 (532994) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 b.8. WICHITA7 (532796) 345.0 kV to WICHTA12_4 (532997) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_218 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.3. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.4. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.5. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.6. WOLFCRK7 (532797) 345.0 kV to WCGS_TX1_1 (533900) 13.8 kV to WCGS_TX1TER1 (533901) 4.0 kV Three Winding #1 b.7. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 b.8. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX9_T1 (533905) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_219 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_220 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_221 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_222 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_223 | Single Phase Fault with Stuck Breaker on NRSS7 345.00 (532777) 345 kV Bus a. Apply Fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHORDGWF7 (532778) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_224 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_225 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_226 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_227 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_228 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_229 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_230 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_231 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.3. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_232 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_233 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.3. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_234 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_235 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_236 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.2. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 b.3. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_REGIONAL_FAULT_237 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Line to Ground Fault on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to Trip Bus #1 b.7. HILLCTY1 (531387) 34.5 kV to Generator #1 b.8. HILLCTY1 (531387) 34.5 kV to Generator #2 b.9. HILLCTY1 (531387) 34.5 kV to Generator #3 b.10. HILLCTY1 (531387) 34.5 kV to Generator #4 b.11. HILLCTY1 (531387) 34.5 kV to Generator #5 b.12. HILLCTY1 (531387) 34.5 kV to Generator #6 b.13. HILLCTY1 (531387) 34.5 kV to Trip Bus # b.14. REDLIN 3 (530605) 115.0 kV to Trip Bus # b.15. HOXIE 3 (530556) 115.0 kV to Trip Bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Line to Ground Fault on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Breaker at From Bus #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Breaker at From Bus #1 b.3. N HAYS3 (530581) 115.0 kV to Trip Bus #1 b.4. VINETAP3 (530693) 115.0 kV to Trip Bus #1 b.5. GMECG1 1 (530674) 13.8 kV to Trip Bus #1 b.6. GMECG2 1 (530675) 13.8 kV to Trip Bus #1 b.7. GMEC 3 (530676) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. ANGUS 3 (530714) 115.0 kV to Trip Bus # b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. GORHAM 3 (530552) 115.0 kV to Load #1 b.8. RUSLPMP3 (530684) 115.0 kV to Load #1 b.9. GORHAM 3 (530552) 115.0 kV to Trip Bus # b.10. RUSLPMP3 (530684) 115.0 kV to Trip Bus # b.11. PFEIFER 3 (530725) 115.0 kV to Load #1 b.12. PFEIFER 3 (530725) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to Trip Bus # b.4. BUCKW_WTG (530708) 0.7 kV to Trip Bus # b.5. BUCKEYE_230 (530702) 230.0 kV to Trip Bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to Trip Bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to Trip Bus # b.8. BUCKW_TERT (530706) 13.8 kV to Trip Bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to Trip Bus # b.10. BUCKE_TERT (530709) 13.8 kV to Trip Bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to None Transmission Circuit #1 b.3. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.4. None to Trip Bus # b.5. SHP234 1 (530604) 34.5 kV to Trip Bus # b.6. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.7. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.4. SMKYP1 6 (530593) 230.0 kV to Trip Bus # b.5. SHP134 1X (530595) 34.5 kV to Trip Bus # b.6. SHP134 1 (530633) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to Trip Bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.7. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.8. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.9. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.10. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on VINEDE_S 115.00 (530722) 115 kV Bus a. Apply fault at the VINEDE_S 115.00 (530722) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.2. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.3. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.4. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on GMEC 3 115.00 (530676) 115 kV Bus a. Apply fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on SMKYP1 6 230.00 (530593) 230 kV Bus a. Apply fault at the SMKYP1 6 230.00 (530593) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.2. SMKYP1 6 (530593) 230.0 kV to SHP134 1 (530633) 34.5 kV to MPT TERT (530726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BUNKRHL3 115.00 (539643) 115 kV Bus a. Apply fault at the BUNKRHL3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.4. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on MACON 3345.00 (640527) 345 kV Bus a. Apply fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MACON 3 (640527) 345.0 kV to LITTLEBLUEW3 (640528) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on G19-053/055 230.00 (763846) 230 kV Bus a. Apply fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on G19-054/068 230.00 (763857) 230 kV Bus a. Apply fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G22-075-TAP (768480) 345.0 kV to GEN-2022-075 (768481) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_082 | 3 Phase fault on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_083 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_084 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_085 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_086 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_087 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_088 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_089 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_090 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_091 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_092 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_093 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_094 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_095 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_096 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_097 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_098 | 3 Phase fault on NRSS7 345.00 (532777) 345 kV Bus a. Apply fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_099 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_100 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_101 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_102 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_103 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_104 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_105 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_106 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_107 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_108 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_109 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_110 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_111 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_112 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_113 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_114 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_115 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_116 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_117 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to PIXLEY-SOLAR (539871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_118 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2018-049 (762834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_119 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_120 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_121 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_122 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3771 (640600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_123 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_124 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_125 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_126 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_127 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_128 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_129 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_130 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_131 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_132 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_133 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_134 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_135 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P1_REGIONAL_FAULT_136 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNLL1 1 (530629) 11.5 kV to KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply Fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.5. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 b.6. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply Fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.5. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.8. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HILLCTY1 (531387) 34.5 kV Two Winding #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.6. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 b.7. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to # b.8. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.6. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.7. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CEDARBLF_COL34.500 (530613) 34.5 kV Bus a. Apply Fault at the CEDARBLF_COL34.500 (530613) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 b.5. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.7. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.5. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.6. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on PRWNDCL1 34.500 (530701) 34.5 kV Bus a. Apply Fault at the PRWNDCL1 34.500 (530701) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.6. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 b.8. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.10. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK3 (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to COLLYER3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to G24-322-TAP (786630) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.6. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.7. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 b.8. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 b.9. CEDAR ST (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.10. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.11. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.12. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.13. CEDAR ST (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.4. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.5. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.7. CDRBLF_13.8 (530611) 13.8 kV to CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV Three Winding #1 b.9. CEDARBLF_FDR (530612) 34.5 kV to CEDARBLF_COL (530613) 34.5 kV Transmission Circuit #1 b.11. CEDARBLF_COL (530613) 34.5 kV to CEDARBLF_GEN (530614) 0.7 kV Two Winding #1 b.12. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.13. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.14. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.16. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.17. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MACON 3345.00 (640527) 345 kV Bus a. Apply Fault at the MACON 3345.00 (640527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-1 (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.8. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.2. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. The issue was also observed in base case with no impact from the CQ unit. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDT1 (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on NWGBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the NWGBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. NWGBEND3 (539681) 115.0 kV to NWGBEND1 (539721) 34.5 kV to NWGBND-1 (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLT1 (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.8. SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.9. SPERVLT1 (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.10. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.12. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLD1 (539936) 13.8 kV Three Winding #1 b.13. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.14. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1 1 (539116) 0.6 kV Two Winding #1 b.15. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on ELLSWTH3 115.00 (539662) 115 kV Bus a. Apply Fault at the ELLSWTH3 115.00 (539662) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. ELLSWTH3 (539662) 115.0 kV to ELLSWTH1 (539708) 34.5 kV to ELSWTH-1 (539908) 13.8 kV Three Winding #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 b.6. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply Fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to BUNKRHL3 (539643) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. BUNKRHL3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.5. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.6. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-1 (539966) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on PLAINVL3 115.00 (539686) 115 kV Bus a. Apply Fault at the PLAINVL3 115.00 (539686) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.2. PHLBURG3 (539685) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 b.3. PLAINVL3 (539686) 115.0 kV to PLAINVL1 (539725) 34.5 kV to PLAINV-1 (539928) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSLSOL3 (539604) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-1 (539943) 7.2 kV Three Winding #1 b.5. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.6. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-1 (539938) 7.2 kV Three Winding #1 b.7. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on ST-JOHN3 115.00 (539696) 115 kV Bus a. Apply Fault at the ST-JOHN3 115.00 (539696) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.2. SADLHRN3 (539010) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. ST-JOHN3 (539696) 115.0 kV to GEN-2024-205 (783121) 115.0 kV Transmission Circuit #1 b.5. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.6. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.7. SADLHRN3 (539010) 115.0 kV to PRICHRD3 (539648) 115.0 kV Transmission Circuit #1 b.8. PRICHRD3 (539648) 115.0 kV to RVROAD 3 (539651) 115.0 kV Transmission Circuit #1 b.9. PRICHRD3 (539648) 115.0 kV to PRATTENERGY3 (539753) 115.0 kV Transmission Circuit #1 b.10. PRICHRD3 (539648) 115.0 kV to ASGI2015-001 (584710) 115.0 kV Transmission Circuit #1 b.11. PRATTENERGY3 (539753) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.12. SEMCRDE3 (539754) 115.0 kV to SKLYVL_GOAB3 (539756) 115.0 kV Transmission Circuit #1 b.13. SEMCRDE3 (539754) 115.0 kV to SEMCRDE1 (539755) 34.5 kV to SEMCRDE-1 (539965) 13.8 kV Three Winding #1 b.14. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.15. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.16. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.17. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 b.4. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 b.5. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 b.7. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.8. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.9. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.10. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.3. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.5. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.4. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on CEDAR_BLU_HV230.00 (930982) 230 kV Bus a. Apply Fault at the CEDAR_BLU_HV230.00 (930982) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDAR_BLU_HV (930982) 230.0 kV Transmission Circuit #1 b.2. CEDAR_BLU_HV (930982) 230.0 kV to CEDAR_BLU_T1 (930984) 34.5 kV to CEDAR_BLU_B1 (930983) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on CEDARBLF_230230.00 (530610) 230 kV Bus a. Apply Fault at the CEDARBLF_230230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.2. CEDARBLF_230 (530610) 230.0 kV to CEDARBLF_FDR (530612) 34.5 kV to CDRBLF_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.5. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.4. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.5. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to MACON 3 (640527) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to GEN-2021-076 (765990) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.4. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.3. G22-065-TAP (768280) 230.0 kV to GEN-2022-065 (768281) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply Fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to NWGBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDT1 (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBND-1 (539921) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.3. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to FRMR CTY WF (635027) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ATCHISON 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHISON 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHISON 3 (635017) 345.0 kV to NORTHBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. ATCHISON 3 (635017) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.3. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.4. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.5. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.6. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3458 3 (645458) 345.0 kV to S3458-HOLT 3 (645558) 345.0 kV Transmission Circuit #z1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #2 b.6. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.8. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.5. G18-125-TAP (763410) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHISON 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_198 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_199 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_200 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_201 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_202 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_203 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_205 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_206 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_207 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_208 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_209 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_211 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_212 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_213 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.8. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_214 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_216 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_217 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.5. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.6. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.7. WICHITA7 (532796) 345.0 kV to WICHTA11_4 (532994) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 b.8. WICHITA7 (532796) 345.0 kV to WICHTA12_4 (532997) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_218 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.3. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.4. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.5. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.6. WOLFCRK7 (532797) 345.0 kV to WCGS_TX1_1 (533900) 13.8 kV to WCGS_TX1TER1 (533901) 4.0 kV Three Winding #1 b.7. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX8_T1 (532962) 13.8 kV Three Winding #1 b.8. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WCGS_TX9_T1 (533905) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_219 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to FR4345KV-TAP (532814) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_220 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_221 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_222 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_223 | Single Phase Fault with Stuck Breaker on NRSS7 345.00 (532777) 345 kV Bus a. Apply Fault at the NRSS7 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRSS7 (532777) 345.0 kV to NEOSHORDGWF7 (532778) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_224 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_225 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_226 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_227 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_228 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_229 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.3. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_230 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_231 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.3. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_232 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_233 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.3. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_234 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_235 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_236 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF1 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #1 b.2. 5MORGAN (300101) 161.0 kV to 5MORGANXF1 (301622) 161.0 kV Transmission Circuit #1 b.3. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_REGIONAL_FAULT_237 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Line to Ground Fault on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to Trip Bus #1 b.7. HILLCTY1 (531387) 34.5 kV to Generator #1 b.8. HILLCTY1 (531387) 34.5 kV to Generator #2 b.9. HILLCTY1 (531387) 34.5 kV to Generator #3 b.10. HILLCTY1 (531387) 34.5 kV to Generator #4 b.11. HILLCTY1 (531387) 34.5 kV to Generator #5 b.12. HILLCTY1 (531387) 34.5 kV to Generator #6 b.13. HILLCTY1 (531387) 34.5 kV to Trip Bus # b.14. REDLIN 3 (530605) 115.0 kV to Trip Bus # b.15. HOXIE 3 (530556) 115.0 kV to Trip Bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Line to Ground Fault on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Breaker at From Bus #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Breaker at From Bus #1 b.3. N HAYS3 (530581) 115.0 kV to Trip Bus #1 b.4. VINETAP3 (530693) 115.0 kV to Trip Bus #1 b.5. GMECG1 1 (530674) 13.8 kV to Trip Bus #1 b.6. GMECG2 1 (530675) 13.8 kV to Trip Bus #1 b.7. GMEC 3 (530676) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. ANGUS 3 (530714) 115.0 kV to Trip Bus # b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. GORHAM 3 (530552) 115.0 kV to Load #1 b.8. RUSLPMP3 (530684) 115.0 kV to Load #1 b.9. GORHAM 3 (530552) 115.0 kV to Trip Bus # b.10. RUSLPMP3 (530684) 115.0 kV to Trip Bus # b.11. PFEIFER 3 (530725) 115.0 kV to Load #1 b.12. PFEIFER 3 (530725) 115.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to Trip Bus # b.4. BUCKW_WTG (530708) 0.7 kV to Trip Bus # b.5. BUCKEYE_230 (530702) 230.0 kV to Trip Bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to Trip Bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to Trip Bus # b.8. BUCKW_TERT (530706) 13.8 kV to Trip Bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to Trip Bus # b.10. BUCKE_TERT (530709) 13.8 kV to Trip Bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to Trip Bus # b.6. KNOLL S 6 (530720) 230.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to None Transmission Circuit #1 b.3. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.4. None to Trip Bus # b.5. SHP234 1 (530604) 34.5 kV to Trip Bus # b.6. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.7. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.4. SMKYP1 6 (530593) 230.0 kV to Trip Bus # b.5. SHP134 1X (530595) 34.5 kV to Trip Bus # b.6. SHP134 1 (530633) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. None to Trip Bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to Trip Bus #1 b.4. SMKYP1V80 (530594) 0.7 kV to Trip Bus #1 b.5. SMKYP2G1 (530600) 0.7 kV to Trip Bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SMOKYHL6 (530592) 230.0 kV to Trip Bus # b.8. SHP134 1X (530595) 34.5 kV to Trip Bus # b.9. SHP234 1 (530604) 34.5 kV to Trip Bus # b.10. SHP134 1 (530633) 34.5 kV to Trip Bus # b.11. SHG2 34 1 (530715) 34.5 kV to Trip Bus # b.12. SMKYP1V100 (530634) 0.7 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to CEDARBLF_230 (530610) 230.0 kV Transmission Circuit #1 b.3. CEDARBLF_GEN (530614) 0.7 kV to Trip Bus # b.4. CEDARBLF_230 (530610) 230.0 kV to Trip Bus # b.5. CDRBLF_13.8 (530611) 13.8 kV to Trip Bus # b.6. CEDARBLF_FDR (530612) 34.5 kV to Trip Bus # b.7. CEDARBLF_COL (530613) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to Trip Bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.7. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.8. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.9. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.10. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to Trip Bus # b.6. BUFLOCRK1 (530689) 34.5 kV to Trip Bus # b.7. PRWINDG1 (530690) 0.7 kV to Trip Bus # b.8. BUFCRKT11 (530691) 12.5 kV to Trip Bus # b.9. PRWNDCL1 (530701) 34.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Base | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Base | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Base | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Base | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29S | Base | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Base | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Base | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Base | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Base | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBND-1 (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.6. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required
03 CENTRAL | GEN-2026-PR7 PISIS CF | 29W | Base | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply Fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the GEN-2024-205 (783124 and 783127) generating sites and voltage oscillations were observed in the St-John substation (539696) and nearby buses in post fault conditions. | No mitigation is required

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR7 | 03 CENTRAL | 930982 | CEDAR_BLU_HV | 230 | 3.0269 | 3.1593 | 0.1324
GEN-2026-PR7 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8393 | 8.9679 | 0.1286
GEN-2026-PR7 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.2937 | 11.3846 | 0.0909
GEN-2026-PR7 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 11.2014 | 11.2903 | 0.0889
GEN-2026-PR7 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.2014 | 11.2903 | 0.0889
GEN-2026-PR7 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.2382 | 8.2845 | 0.0463
GEN-2026-PR7 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 11.1407 | 11.1814 | 0.0407
GEN-2026-PR7 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.441 | 8.4807 | 0.0397
GEN-2026-PR7 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.3538 | 8.3906 | 0.0368
GEN-2026-PR7 | 03 CENTRAL | 765990 | GEN-2021-076 | 345 | 8.3538 | 8.3906 | 0.0368
GEN-2026-PR7 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.5834 | 10.6196 | 0.0362
GEN-2026-PR7 | 03 CENTRAL | 530581 | N HAYS3 | 115 | 9.7571 | 9.7918 | 0.0347
GEN-2026-PR7 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.2581 | 8.2925 | 0.0344
GEN-2026-PR7 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 7.747 | 7.7773 | 0.0303
GEN-2026-PR7 | 03 CENTRAL | 530694 | VINE2 3 | 115 | 7.6746 | 7.7043 | 0.0297
GEN-2026-PR7 | 03 CENTRAL | 530721 | VINEDE_N | 115 | 7.6734 | 7.7031 | 0.0297
GEN-2026-PR7 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.6746 | 7.7043 | 0.0297
GEN-2026-PR7 | 03 CENTRAL | 530562 | CEDAR ST | 115 | 7.5355 | 7.5642 | 0.0287
GEN-2026-PR7 | 03 CENTRAL | 768480 | G22-075-TAP | 345 | 8.1032 | 8.1305 | 0.0273
GEN-2026-PR7 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.5703 | 8.5944 | 0.0241
GEN-2026-PR7 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.5223 | 8.546 | 0.0237
GEN-2026-PR7 | 03 CENTRAL | 768481 | GEN-2022-075 | 345 | 7.1945 | 7.2159 | 0.0214
GEN-2026-PR7 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 13.3698 | 13.3889 | 0.0191
GEN-2026-PR7 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 13.2447 | 13.2636 | 0.0189
GEN-2026-PR7 | 03 CENTRAL | 530610 | CEDARBLF_230 | 230 | 3.5124 | 3.5285 | 0.0161
GEN-2026-PR7 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.2899 | 5.3056 | 0.0157
GEN-2026-PR7 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 15.1209 | 15.1342 | 0.0133
GEN-2026-PR7 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 14.4239 | 14.4356 | 0.0117
GEN-2026-PR7 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.787 | 6.7984 | 0.0114
GEN-2026-PR7 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.7013 | 6.7125 | 0.0112
GEN-2026-PR7 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 13.0065 | 13.0158 | 0.0093
GEN-2026-PR7 | 03 CENTRAL | 539681 | NWGBEND3 | 115 | 8.6843 | 8.6924 | 0.0081
GEN-2026-PR7 | 03 CENTRAL | 765910 | GEN-2021-068 | 345 | 13.2399 | 13.2479 | 0.008
GEN-2026-PR7 | 03 CENTRAL | 765911 | G21-068-TAP | 345 | 13.3012 | 13.3092 | 0.008
GEN-2026-PR7 | 03 CENTRAL | 765920 | GEN-2021-069 | 345 | 13.2399 | 13.2479 | 0.008
GEN-2026-PR7 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 8.3516 | 8.3592 | 0.0076
GEN-2026-PR7 | 03 CENTRAL | 539831 | WESTPLN7 | 345 | 11.815 | 11.8226 | 0.0076
GEN-2026-PR7 | 03 CENTRAL | 530551 | SALINE 3 | 115 | 5.08 | 5.0871 | 0.0071
GEN-2026-PR7 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4572 | 3.4639 | 0.0067
GEN-2026-PR7 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 12.2082 | 12.2149 | 0.0067
GEN-2026-PR7 | 03 CENTRAL | 765930 | GEN-2021-070 | 345 | 12.1058 | 12.1123 | 0.0065
GEN-2026-PR7 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 9.9206 | 9.9268 | 0.0062
GEN-2026-PR7 | 03 CENTRAL | 768280 | G22-065-TAP | 230 | 6.3379 | 6.3439 | 0.006
GEN-2026-PR7 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 9.7332 | 9.7391 | 0.0059
GEN-2026-PR7 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 7.9907 | 7.9966 | 0.0059
GEN-2026-PR7 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.4223 | 6.4282 | 0.0059
GEN-2026-PR7 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3348 | 13.3407 | 0.0059
GEN-2026-PR7 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.18 | 3.1857 | 0.0057
GEN-2026-PR7 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.3455 | 6.3512 | 0.0057
GEN-2026-PR7 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.4979 | 6.5033 | 0.0054
GEN-2026-PR7 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 6.4979 | 6.5033 | 0.0054
GEN-2026-PR7 | 03 CENTRAL | 640527 | MACON 3 | 345 | 7.2439 | 7.2492 | 0.0053
GEN-2026-PR7 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 27.0373 | 27.0424 | 0.0051
GEN-2026-PR7 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 9.2589 | 9.2639 | 0.005
GEN-2026-PR7 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 26.3146 | 26.3193 | 0.0047
GEN-2026-PR7 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 8.5895 | 8.5941 | 0.0046
GEN-2026-PR7 | 03 CENTRAL | 530590 | BEMIS 3 | 115 | 4.0663 | 4.0708 | 0.0045
GEN-2026-PR7 | 03 CENTRAL | 768281 | GEN-2022-065 | 230 | 5.4329 | 5.4374 | 0.0045
GEN-2026-PR7 | 03 CENTRAL | 539823 | IRONSTAR7 | 345 | 10.524 | 10.5284 | 0.0044
GEN-2026-PR7 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.9906 | 9.995 | 0.0044
GEN-2026-PR7 | 03 CENTRAL | 533416 | RENO 3 | 115 | 29.5297 | 29.5339 | 0.0042
GEN-2026-PR7 | 03 CENTRAL | 533419 | HEC 3 | 115 | 24.6961 | 24.7003 | 0.0042
GEN-2026-PR7 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3605 | 11.3647 | 0.0042
GEN-2026-PR7 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 15.5277 | 15.5318 | 0.0041
GEN-2026-PR7 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.2269 | 11.231 | 0.0041
GEN-2026-PR7 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 10.8588 | 10.8626 | 0.0038
GEN-2026-PR7 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 5.8662 | 5.8699 | 0.0037
GEN-2026-PR7 | 03 CENTRAL | 640528 | LITTLEBLUEW3 | 345 | 6.0997 | 6.1034 | 0.0037
GEN-2026-PR7 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.9235 | 9.9271 | 0.0036
GEN-2026-PR7 | 03 CENTRAL | 539686 | PLAINVL3 | 115 | 3.8041 | 3.8075 | 0.0034
GEN-2026-PR7 | 03 CENTRAL | 999982 | ZSWSH_999982 | 115 | 3.8041 | 3.8075 | 0.0034
GEN-2026-PR7 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 14.2403 | 14.2435 | 0.0032
GEN-2026-PR7 | 03 CENTRAL | 530605 | REDLIN 3 | 115 | 4.0185 | 4.0216 | 0.0031
GEN-2026-PR7 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 19.0048 | 19.0079 | 0.0031
GEN-2026-PR7 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 19.7005 | 19.7035 | 0.003
GEN-2026-PR7 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 5.2719 | 5.2749 | 0.003
GEN-2026-PR7 | 03 CENTRAL | 786630 | G24-322-TAP | 115 | 3.9752 | 3.9782 | 0.003
GEN-2026-PR7 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 7.1139 | 7.1168 | 0.0029
GEN-2026-PR7 | 03 CENTRAL | 786631 | GEN-2024-322 | 115 | 3.9584 | 3.9613 | 0.0029
GEN-2026-PR7 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.3864 | 9.3892 | 0.0028
GEN-2026-PR7 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 8.5876 | 8.5903 | 0.0027
GEN-2026-PR7 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 8.5876 | 8.5903 | 0.0027
GEN-2026-PR7 | 03 CENTRAL | 539824 | IRS7 115 KV | 115 | 15.1931 | 15.1958 | 0.0027
GEN-2026-PR7 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.3845 | 9.3872 | 0.0027
GEN-2026-PR7 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.6842 | 2.6866 | 0.0024
GEN-2026-PR7 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.0892 | 2.0916 | 0.0024
GEN-2026-PR7 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7307 | 8.7331 | 0.0024
GEN-2026-PR7 | 03 CENTRAL | 764420 | GEN-2020-011 | 345 | 9.2024 | 9.2048 | 0.0024
GEN-2026-PR7 | 03 CENTRAL | 764430 | G20-011-TAP | 345 | 9.2024 | 9.2048 | 0.0024
GEN-2026-PR7 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2308 | 10.2331 | 0.0023
GEN-2026-PR7 | 03 CENTRAL | 764431 | G20-011-SS1 | 345 | 9.1928 | 9.1951 | 0.0023
GEN-2026-PR7 | 03 CENTRAL | 764433 | G20-011-SS3 | 345 | 9.1218 | 9.1241 | 0.0023
GEN-2026-PR7 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.2624 | 6.2646 | 0.0022
GEN-2026-PR7 | 03 CENTRAL | 764432 | G20-011-SS2 | 345 | 9.091 | 9.0932 | 0.0022
GEN-2026-PR7 | 03 CENTRAL | 764434 | G20-011-SS4 | 345 | 8.9453 | 8.9475 | 0.0022
GEN-2026-PR7 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8037 | 5.8058 | 0.0021
GEN-2026-PR7 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 9.7244 | 9.7264 | 0.002
GEN-2026-PR7 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 13.7167 | 13.7186 | 0.0019
GEN-2026-PR7 | 03 CENTRAL | 765340 | GEN-2021-005 | 345 | 13.376 | 13.3779 | 0.0019
GEN-2026-PR7 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1572 | 5.159 | 0.0018
GEN-2026-PR7 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 15.1526 | 15.1544 | 0.0018
GEN-2026-PR7 | 03 CENTRAL | 530560 | WKNNY 3 | 115 | 2.2631 | 2.2648 | 0.0017
GEN-2026-PR7 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.1978 | 5.1994 | 0.0016
GEN-2026-PR7 | 03 CENTRAL | 531492 | OG ONEOK3 | 115 | 2.1829 | 2.1844 | 0.0015
GEN-2026-PR7 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.3468 | 4.3481 | 0.0013
GEN-2026-PR7 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 11.7599 | 11.7611 | 0.0012
GEN-2026-PR7 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.2249 | 4.226 | 0.0011
GEN-2026-PR7 | 03 CENTRAL | 531497 | COLLYER3 | 115 | 1.8245 | 1.8256 | 0.0011
GEN-2026-PR7 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 11.5021 | 11.5032 | 0.0011
GEN-2026-PR7 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 3.1202 | 3.1213 | 0.0011
GEN-2026-PR7 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 8.6692 | 8.6703 | 0.0011
GEN-2026-PR7 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.7588 | 3.7598 | 0.001
GEN-2026-PR7 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.2979 | 4.2989 | 0.001
GEN-2026-PR7 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2838 | 5.2847 | 0.0009
GEN-2026-PR7 | 03 CENTRAL | 585241 | GEN-2015-088 | 345 | 16.2679 | 16.2688 | 0.0009
GEN-2026-PR7 | 03 CENTRAL | 783121 | GEN-2024-205 | 115 | 5.2545 | 5.2554 | 0.0009
GEN-2026-PR7 | 03 CENTRAL | 530623 | RICE 3 | 115 | 7.4314 | 7.4322 | 0.0008
GEN-2026-PR7 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.8121 | 3.8128 | 0.0007
GEN-2026-PR7 | 03 CENTRAL | 539604 | RUSLSOL3 | 115 | 3.7622 | 3.7629 | 0.0007
GEN-2026-PR7 | 03 CENTRAL | 539643 | BUNKRHL3 | 115 | 3.9178 | 3.9185 | 0.0007
GEN-2026-PR7 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.7682 | 3.7689 | 0.0007
GEN-2026-PR7 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.7361 | 4.7367 | 0.0006
GEN-2026-PR7 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 9.3049 | 9.3055 | 0.0006
GEN-2026-PR7 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 5.3235 | 5.324 | 0.0005
GEN-2026-PR7 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.6737 | 8.6742 | 0.0005
GEN-2026-PR7 | 03 CENTRAL | 532999 | GEN-2016-111 | 345 | 7.5247 | 7.5252 | 0.0005
GEN-2026-PR7 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 7.825 | 7.8255 | 0.0005
GEN-2026-PR7 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.5127 | 3.5131 | 0.0004
GEN-2026-PR7 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.9452 | 2.9456 | 0.0004
GEN-2026-PR7 | 03 CENTRAL | 643330 | PH-WIND | 345 | 5.9652 | 5.9656 | 0.0004
GEN-2026-PR7 | 03 CENTRAL | 999983 | ZSWSH_999983 | 115 | 3.7599 | 3.7603 | 0.0004
GEN-2026-PR7 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 3.0682 | 3.0685 | 0.0003
GEN-2026-PR7 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6763 | 1.6765 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.4033 | 2.4035 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.2079 | 2.2081 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 5.2269 | 5.2271 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.8649 | 5.8651 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 7.0698 | 7.07 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 533513 | HEC 2 | 69 | 7.5099 | 7.5101 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 643370 | GEN-17-181B1 | 345 | 7.2195 | 7.2197 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 643371 | GEN-2017-181 | 345 | 7.2195 | 7.2197 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 643377 | GEN-2017-182 | 345 | 7.2195 | 7.2197 | 0.0002
GEN-2026-PR7 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2717 | 1.2718 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1526 | 1.1527 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.5125 | 1.5126 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 530591 | J-HAWK 2 | 69 | 1.038 | 1.0381 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.6476 | 1.6477 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.9212 | 3.9213 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533502 | CESSNA 2 | 69 | 4.7693 | 4.7694 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533503 | CESSNAJ2 | 69 | 4.8381 | 4.8382 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533507 | 18&PLUM2 | 69 | 4.9522 | 4.9523 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533509 | 11HALST2 | 69 | 5.6681 | 5.6682 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533511 | 14LORAN2 | 69 | 5.3078 | 5.3079 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.0627 | 6.0628 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533522 | 17HUXMN2 | 69 | 5.4678 | 5.4679 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 533523 | 17 PLUM2 | 69 | 5.0063 | 5.0064 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 640314 | PAULINE8 | 69 | 4.9584 | 4.9585 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 640448 | HOLDREGE 8 | 69 | 3.9326 | 3.9327 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 764435 | GEN-2020-013 | 115 | 3.2669 | 3.267 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 764446 | G20-013-SS1 | 115 | 3.2626 | 3.2627 | 0.0001
GEN-2026-PR7 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.533 | 1.533 | 0
GEN-2026-PR7 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.5857 | 1.5857 | 0
GEN-2026-PR7 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4912 | 3.4912 | 0
GEN-2026-PR7 | 03 CENTRAL | 640310 | ORLEANS7 | 115 | 2.0382 | 2.0382 | 0
GEN-2026-PR7 | 03 CENTRAL | 640311 | ORLEANS8 | 69 | 2.5191 | 2.5191 | 0
GEN-2026-PR7 | 03 CENTRAL | 764445 | G20-013-TAP | 115 | 3.27 | 3.27 | 0
GEN-2026-PR7 | 03 CENTRAL | 764447 | G20-013-SS2 | 115 | 3.1833 | 3.1833 | 0
GEN-2026-PR7 | 03 CENTRAL | 764448 | G20-013-SS3 | 115 | 3.1672 | 3.1672 | 0

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
03 CENTRAL | GEN-2026-PR7 | 5.6687 | PASS | 0.34455 | PASS | N/A | N/A | No

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | BASE CASE | 11.9494 | PASS | 0.34456 | PASS | 244.5598 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530552 [GORHAM 3 115.00] TO BUS 530714 [ANGUS 3 115.00] CKT 1 | 11.9468 | PASS | 0.34457 | PASS | 244.5749 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530695 [CHETOLAH3 115.00] CKT 1 | 11.4518 | PASS | 0.34486 | PASS | 244.8611 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530714 [ANGUS 3 115.00] CKT 1 | 11.9441 | PASS | 0.34458 | PASS | 244.5838 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530725 [PFEIFER 3 115.00] CKT 1 | 11.946 | PASS | 0.34457 | PASS | 244.5682 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530558 [KNOLL N 6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 11.9462 | PASS | 0.34456 | PASS | 244.5621 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530558 [KNOLL N 6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 1 | 11.9481 | PASS | 0.34456 | PASS | 244.5602 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530581 [N HAYS3 115.00] CKT 1 | 11.5004 | PASS | 0.34476 | PASS | 244.7556 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530581 [N HAYS3 115.00] TO BUS 530695 [CHETOLAH3 115.00] CKT 1 | 11.4909 | PASS | 0.34477 | PASS | 244.7746 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 5.8984 | PASS | 0.35061 | PASS | 250.6111 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [CEDARBLF_230 230.00] CKT 1 | 12.0408 | PASS | 0.34477 | PASS | 244.7708 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 8.6542 | PASS | 0.3467 | PASS | 246.6982 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 640527 [MACON 3 345.00] CKT 1 | 10.4764 | PASS | 0.34504 | PASS | 245.044 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076 345.00] CKT 1 | 11.9495 | PASS | 0.34456 | PASS | 244.5604 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 10.2494 | PASS | 0.34541 | PASS | 245.4132 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 11.9066 | PASS | 0.34471 | PASS | 244.7063 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 11.9465 | PASS | 0.34456 | PASS | 244.5619 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 1 | 10.8724 | PASS | 0.34512 | PASS | 245.1218 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 11.9115 | PASS | 0.34457 | PASS | 244.5721 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.8397 | PASS | 0.34462 | PASS | 244.6209 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530693 [VINETAP3 115.00] TO BUS 530695 [CHETOLAH3 115.00] CKT 1 | 11.9495 | PASS | 0.34456 | PASS | 244.5599 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530695 [CHETOLAH3 115.00] TO BUS 530722 [VINEDE_S 115.00] CKT 1 | 11.9359 | PASS | 0.34458 | PASS | 244.5781 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 11.2986 | PASS | 0.34483 | PASS | 244.8326 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 11.8905 | PASS | 0.34459 | PASS | 244.595 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539666 [GBENDTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 11.8902 | PASS | 0.34459 | PASS | 244.5939 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [NWGBEND3 115.00] CKT 1 | 11.9397 | PASS | 0.34457 | PASS | 244.5746 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 11.9483 | PASS | 0.34456 | PASS | 244.5618 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 11.2822 | PASS | 0.34486 | PASS | 244.8582 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 11.649 | PASS | 0.34475 | PASS | 244.7456 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763850 [G19-055-TAP 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 11.6545 | PASS | 0.34473 | PASS | 244.7259 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763857 [G19-054/068 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 11.9264 | PASS | 0.34459 | PASS | 244.5904 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768280 [G22-065-TAP 230.00] TO BUS 768281 [GEN-2022-065 230.00] CKT 1 | 11.9589 | PASS | 0.34455 | PASS | 244.5483 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530552 [GORHAM 3 115.00] TO BUS 530684 [RUSLPMP3 115.00] CKT 1 | 11.9497 | PASS | 0.34456 | PASS | 244.5643 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530582 [S HAYS6 230.00] CKT 1 | 11.4477 | PASS | 0.3449 | PASS | 244.9034 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530558 [KNOLL N 6 230.00] TO BUS 530561 [KNOLL 3 115.00] CKT 1 | 11.9148 | PASS | 0.34461 | PASS | 244.6086 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530551 [SALINE 3 115.00] CKT 1 | 11.805 | PASS | 0.34467 | PASS | 244.6705 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530605 [REDLIN 3 115.00] CKT 1 | 11.7836 | PASS | 0.34467 | PASS | 244.6733 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530676 [GMEC 3 115.00] CKT 1 | 11.4763 | PASS | 0.34468 | PASS | 244.6822 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530677 [OGALATP3 115.00] CKT 1 | 11.9434 | PASS | 0.34457 | PASS | 244.5692 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 7.6048 | PASS | 0.34695 | PASS | 246.9504 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 530593 [SMKYP1 6 230.00] CKT 1 | 11.9452 | PASS | 0.34459 | PASS | 244.5942 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 532873 [SUMMIT 6 230.00] CKT 1 | 10.7878 | PASS | 0.34494 | PASS | 244.9356 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 530604 [SHP234 1 34.5.00] CKT 1 | 11.9585 | PASS | 0.34457 | PASS | 244.5742 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530602 [LAXTAP 3 115.00] CKT 1 | 11.9241 | PASS | 0.34457 | PASS | 244.5707 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530609 [HZRNGPL3 115.00] CKT 1 | 11.9483 | PASS | 0.34456 | PASS | 244.5608 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530680 [HEIZER 6 230.00] CKT 1 | 11.8397 | PASS | 0.34462 | PASS | 244.6208 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530563 [HEIZER 2 69.00] CKT 2 | 11.9479 | PASS | 0.34456 | PASS | 244.562 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530563 [HEIZER 2 69.00] CKT 3 | 11.9479 | PASS | 0.34456 | PASS | 244.5622 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530610 [CEDARBLF_230 230.00] TO BUS 530612 [CEDARBLF_FDR 34.5.00] CKT 1 | 12.0261 | PASS | 0.34474 | PASS | 244.7443 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530693 [VINETAP3 115.00] TO BUS 530721 [VINEDE_N 115.00] CKT 1 | 11.9494 | PASS | 0.34456 | PASS | 244.5598 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530702 [BUCKEYE_230 230.00] TO BUS 530703 [BUCKEYE_E1 34.5.00] CKT 1 | 11.9273 | PASS | 0.34463 | PASS | 244.6282 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530702 [BUCKEYE_230 230.00] TO BUS 530710 [BUCKEYE_W1 34.5.00] CKT 1 | 11.9323 | PASS | 0.34463 | PASS | 244.6259 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530722 [VINEDE_S 115.00] TO BUS 530562 [CEDAR ST 115.00] CKT 1 | 11.9453 | PASS | 0.34456 | PASS | 244.5642 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530722 [VINEDE_S 115.00] TO BUS 530694 [VINE2 3 115.00] CKT 1 | 11.9399 | PASS | 0.34457 | PASS | 244.5735 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 530686 [RICE 6 230.00] CKT 1 | 11.9488 | PASS | 0.34457 | PASS | 244.5653 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 532872 [EMCPHER6 230.00] CKT 1 | 11.9179 | PASS | 0.34458 | PASS | 244.5765 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 533413 [CIRCLE 3 115.00] CKT 1 | 11.7735 | PASS | 0.34461 | PASS | 244.6063 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [BUNKRHL3 115.00] CKT 1 | 11.9158 | PASS | 0.34457 | PASS | 244.5748 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 11.9375 | PASS | 0.34457 | PASS | 244.5731 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539666 [GBENDTP3 115.00] TO BUS 539692 [SEWARD 3 115.00] CKT 1 | 11.8902 | PASS | 0.34459 | PASS | 244.593 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.8.00] CKT 1 | 11.6624 | PASS | 0.34459 | PASS | 244.5937 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.5.00] CKT 1 | 11.9478 | PASS | 0.34456 | PASS | 244.5604 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.839 | PASS | 0.34462 | PASS | 244.6207 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539681 [NWGBEND3 115.00] TO BUS 539661 [24-FREY3 115.00] CKT 1 | 11.9433 | PASS | 0.34457 | PASS | 244.5674 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539681 [NWGBEND3 115.00] TO BUS 539721 [NWGBEND1 34.5.00] CKT 1 | 11.9454 | PASS | 0.34457 | PASS | 244.5667 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539684 [OTISSUB3 115.00] TO BUS 539723 [OTISSUB1 34.5.00] CKT 2 | 11.9494 | PASS | 0.34456 | PASS | 244.5597 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539684 [OTISSUB3 115.00] TO BUS 539723 [OTISSUB1 34.5.00] CKT 1 | 11.9494 | PASS | 0.34456 | PASS | 244.5601 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 640527 [MACON 3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.4465 | PASS | 0.34492 | PASS | 244.9191 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 640527 [MACON 3 345.00] TO BUS 640528 [LITTLEBLUEW3 345.00] CKT 1 | 11.9434 | PASS | 0.34459 | PASS | 244.5891 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763850 [G19-055-TAP 230.00] TO BUS 539695 [SPEARVL6 230.00] CKT 1 | 11.6594 | PASS | 0.34471 | PASS | 244.7129 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763850 [G19-055-TAP 230.00] TO BUS 763846 [G19-053/055 230.00] CKT 1 | 11.9541 | PASS | 0.34455 | PASS | 244.555 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763857 [G19-054/068 230.00] TO BUS 763858 [G19-054-XFM1 34.5.00] CKT 1 | 11.9355 | PASS | 0.34458 | PASS | 244.5802 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763857 [G19-054/068 230.00] TO BUS 763968 [G19-068-XFM1 34.5.00] CKT 1 | 11.9466 | PASS | 0.34456 | PASS | 244.5629 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 765990 [GEN-2021-076 345.00] TO BUS 765994 [G21-076-XFM1 34.5.00] CKT 1 | 11.9495 | PASS | 0.34456 | PASS | 244.5604 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768281 [GEN-2022-065 230.00] TO BUS 768282 [G22-065XFMR1 34.5.00] CKT 1 | 11.9588 | PASS | 0.34455 | PASS | 244.548 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768480 [G22-075-TAP 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 10.2844 | PASS | 0.3453 | PASS | 245.3025 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29SP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768480 [G22-075-TAP 345.00] TO BUS 768481 [GEN-2022-075 345.00] CKT 1 | 11.946 | PASS | 0.34461 | PASS | 244.6058 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | BASE CASE | 11.2889 | PASS | 0.34461 | PASS | 244.6145 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530552 [GORHAM 3 115.00] TO BUS 530714 [ANGUS 3 115.00] CKT 1 | 11.2863 | PASS | 0.34463 | PASS | 244.6334 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530695 [CHETOLAH3 115.00] CKT 1 | 10.9747 | PASS | 0.34485 | PASS | 244.8493 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530714 [ANGUS 3 115.00] CKT 1 | 11.2849 | PASS | 0.34464 | PASS | 244.6403 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530725 [PFEIFER 3 115.00] CKT 1 | 11.2846 | PASS | 0.34462 | PASS | 244.6243 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530558 [KNOLL N 6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 11.2871 | PASS | 0.34462 | PASS | 244.6164 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530558 [KNOLL N 6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 1 | 11.2867 | PASS | 0.34462 | PASS | 244.6153 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530581 [N HAYS3 115.00] CKT 1 | 10.9874 | PASS | 0.34479 | PASS | 244.7851 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530581 [N HAYS3 115.00] TO BUS 530695 [CHETOLAH3 115.00] CKT 1 | 10.9845 | PASS | 0.3448 | PASS | 244.8003 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 5.6687 | PASS | 0.35101 | PASS | 251.0125 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [CEDARBLF_230 230.00] CKT 1 | 11.399 | PASS | 0.34482 | PASS | 244.8183 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 8.1384 | PASS | 0.34694 | PASS | 246.9352 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 640527 [MACON 3 345.00] CKT 1 | 9.7358 | PASS | 0.34525 | PASS | 245.2467 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076 345.00] CKT 1 | 11.2891 | PASS | 0.34462 | PASS | 244.6154 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 9.5678 | PASS | 0.34553 | PASS | 245.5347 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 11.2518 | PASS | 0.34477 | PASS | 244.7739 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 11.2873 | PASS | 0.34462 | PASS | 244.6163 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 1 | 10.2548 | PASS | 0.34523 | PASS | 245.2301 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 11.2566 | PASS | 0.34463 | PASS | 244.6289 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.1879 | PASS | 0.34468 | PASS | 244.683 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530693 [VINETAP3 115.00] TO BUS 530695 [CHETOLAH3 115.00] CKT 1 | 11.289 | PASS | 0.34461 | PASS | 244.6147 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530695 [CHETOLAH3 115.00] TO BUS 530722 [VINEDE_S 115.00] CKT 1 | 11.2821 | PASS | 0.34463 | PASS | 244.6308 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 10.7421 | PASS | 0.34487 | PASS | 244.8658 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 11.2436 | PASS | 0.34465 | PASS | 244.6468 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539666 [GBENDTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 11.2365 | PASS | 0.34465 | PASS | 244.6506 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [NWGBEND3 115.00] CKT 1 | 11.2837 | PASS | 0.34463 | PASS | 244.6273 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 11.2883 | PASS | 0.34462 | PASS | 244.6164 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 10.7066 | PASS | 0.34494 | PASS | 244.9391 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 10.9634 | PASS | 0.34484 | PASS | 244.8438 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763850 [G19-055-TAP 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 10.9639 | PASS | 0.34482 | PASS | 244.8224 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763857 [G19-054/068 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 11.2525 | PASS | 0.34468 | PASS | 244.6798 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768280 [G22-065-TAP 230.00] TO BUS 768281 [GEN-2022-065 230.00] CKT 1 | 11.2897 | PASS | 0.34461 | PASS | 244.614 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530552 [GORHAM 3 115.00] TO BUS 530684 [RUSLPMP3 115.00] CKT 1 | 11.2894 | PASS | 0.34462 | PASS | 244.6205 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530553 [S HAYS 3 115.00] TO BUS 530582 [S HAYS6 230.00] CKT 1 | 10.9736 | PASS | 0.34489 | PASS | 244.8855 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530558 [KNOLL N 6 230.00] TO BUS 530561 [KNOLL 3 115.00] CKT 1 | 11.3193 | PASS | 0.34459 | PASS | 244.5918 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530551 [SALINE 3 115.00] CKT 1 | 11.1187 | PASS | 0.34475 | PASS | 244.7495 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530605 [REDLIN 3 115.00] CKT 1 | 11.0933 | PASS | 0.34475 | PASS | 244.7491 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530676 [GMEC 3 115.00] CKT 1 | 11.2882 | PASS | 0.34462 | PASS | 244.6151 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530561 [KNOLL 3 115.00] TO BUS 530677 [OGALATP3 115.00] CKT 1 | 11.2843 | PASS | 0.34463 | PASS | 244.6285 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 6.7615 | PASS | 0.34751 | PASS | 247.5135 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 530593 [SMKYP1 6 230.00] CKT 1 | 11.2942 | PASS | 0.34465 | PASS | 244.65 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 532873 [SUMMIT 6 230.00] CKT 1 | 10.1742 | PASS | 0.34498 | PASS | 244.9827 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530592 [SMOKYHL6 230.00] TO BUS 530604 [SHP234 1 34.5.00] CKT 1 | 11.2984 | PASS | 0.34462 | PASS | 244.6235 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530602 [LAXTAP 3 115.00] CKT 1 | 11.2631 | PASS | 0.34463 | PASS | 244.6272 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530609 [HZRNGPL3 115.00] CKT 1 | 11.2874 | PASS | 0.34461 | PASS | 244.6144 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530680 [HEIZER 6 230.00] CKT 1 | 11.1879 | PASS | 0.34468 | PASS | 244.6828 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530563 [HEIZER 2 69.00] CKT 2 | 11.2878 | PASS | 0.34462 | PASS | 244.6164 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530601 [HEIZER 3 115.00] TO BUS 530563 [HEIZER 2 69.00] CKT 3 | 11.2878 | PASS | 0.34462 | PASS | 244.6166 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530610 [CEDARBLF_230 230.00] TO BUS 530612 [CEDARBLF_FDR 34.5.00] CKT 1 | 11.3824 | PASS | 0.34478 | PASS | 244.7786 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530693 [VINETAP3 115.00] TO BUS 530721 [VINEDE_N 115.00] CKT 1 | 11.2889 | PASS | 0.34461 | PASS | 244.6146 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530702 [BUCKEYE_230 230.00] TO BUS 530703 [BUCKEYE_E1 34.5.00] CKT 1 | 11.2711 | PASS | 0.34468 | PASS | 244.6844 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530702 [BUCKEYE_230 230.00] TO BUS 530710 [BUCKEYE_W1 34.5.00] CKT 1 | 11.2703 | PASS | 0.34469 | PASS | 244.6917 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530722 [VINEDE_S 115.00] TO BUS 530562 [CEDAR ST 115.00] CKT 1 | 11.2863 | PASS | 0.34462 | PASS | 244.6193 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 530722 [VINEDE_S 115.00] TO BUS 530694 [VINE2 3 115.00] CKT 1 | 11.2846 | PASS | 0.34463 | PASS | 244.6257 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 530686 [RICE 6 230.00] CKT 1 | 11.2862 | PASS | 0.34463 | PASS | 244.6263 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 532872 [EMCPHER6 230.00] CKT 1 | 11.2581 | PASS | 0.34463 | PASS | 244.6323 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 532871 [CIRCLE 6 230.00] TO BUS 533413 [CIRCLE 3 115.00] CKT 1 | 11.1417 | PASS | 0.34465 | PASS | 244.6494 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [BUNKRHL3 115.00] CKT 1 | 11.2619 | PASS | 0.34463 | PASS | 244.632 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 11.2808 | PASS | 0.34462 | PASS | 244.6232 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539666 [GBENDTP3 115.00] TO BUS 539692 [SEWARD 3 115.00] CKT 1 | 11.2365 | PASS | 0.34465 | PASS | 244.6504 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.8.00] CKT 1 | 10.9619 | PASS | 0.34467 | PASS | 244.6666 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.5.00] CKT 1 | 11.2882 | PASS | 0.34461 | PASS | 244.6138 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.1801 | PASS | 0.34466 | PASS | 244.6648 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539681 [NWGBEND3 115.00] TO BUS 539661 [24-FREY3 115.00] CKT 1 | 11.2855 | PASS | 0.34462 | PASS | 244.6204 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539681 [NWGBEND3 115.00] TO BUS 539721 [NWGBEND1 34.5.00] CKT 1 | 11.2871 | PASS | 0.34462 | PASS | 244.6208 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539684 [OTISSUB3 115.00] TO BUS 539723 [OTISSUB1 34.5.00] CKT 2 | 11.2889 | PASS | 0.34461 | PASS | 244.6146 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 539684 [OTISSUB3 115.00] TO BUS 539723 [OTISSUB1 34.5.00] CKT 1 | 11.2888 | PASS | 0.34461 | PASS | 244.6149 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 640527 [MACON 3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 9.7027 | PASS | 0.3451 | PASS | 245.0977 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 640527 [MACON 3 345.00] TO BUS 640528 [LITTLEBLUEW3 345.00] CKT 1 | 11.2942 | PASS | 0.34463 | PASS | 244.6309 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763850 [G19-055-TAP 230.00] TO BUS 539695 [SPEARVL6 230.00] CKT 1 | 10.9734 | PASS | 0.3448 | PASS | 244.8028 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763850 [G19-055-TAP 230.00] TO BUS 763846 [G19-053/055 230.00] CKT 1 | 11.2876 | PASS | 0.34462 | PASS | 244.6187 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763857 [G19-054/068 230.00] TO BUS 763858 [G19-054-XFM1 34.5.00] CKT 1 | 11.2651 | PASS | 0.34466 | PASS | 244.6615 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 763857 [G19-054/068 230.00] TO BUS 763968 [G19-068-XFM1 34.5.00] CKT 1 | 11.2801 | PASS | 0.34463 | PASS | 244.6292 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 765990 [GEN-2021-076 345.00] TO BUS 765994 [G21-076-XFM1 34.5.00] CKT 1 | 11.2891 | PASS | 0.34462 | PASS | 244.6154 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768281 [GEN-2022-065 230.00] TO BUS 768282 [G22-065XFMR1 34.5.00] CKT 1 | 11.2896 | PASS | 0.34461 | PASS | 244.6134 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768480 [G22-075-TAP 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 9.5895 | PASS | 0.34544 | PASS | 245.4396 | 39.76 | 46.95
GEN-2026-PR7 PSIS | 03 CENTRAL | 29WP | GEN-2026-PR7 | 230kV Bus at MIDW SOUTH HAYS Substation, Brownell County, KS | OPEN LINE FROM BUS 768480 [G22-075-TAP 345.00] TO BUS 768481 [GEN-2022-075 345.00] CKT 1 | 11.2861 | PASS | 0.34467 | PASS | 244.6692 | 39.76 | 46.95

## WSCR
* WSCR is not applicable for this study.